# Maintenance Schedule for Air Distribution Systems

| Description | Comments | Maintenance Frequency |
| --- | --- | --- |
| Fill out daily log | Check all setpoints such as pressure and temperature for proper setting and function. | Daily |
| Overall inspection | Inspect the unit to ensure it is operating in a “normal” condition for vibration, noise, and odors. Verify gauges and thermometers are reading within range. Inspect for leakage due to access doors not being properly closed. Verify that any internal lighting is off. Verify all safety guards are in place. | Daily |
| Inspect pulleys and belts | Inspect belt tension and alignment. Look for rubber shavings under the pulleys. | Weekly |
| Grease fan and motor bearings | Inspect visible grease for metal shavings, indicating a possible failing bearing. Wipe away all excess grease after greasing. Inspect grease tubing if installed for integrity to make sure grease is getting to the bearings. Check bearings for excessive heat, noise, or vibration. | Semi-annually |
| Fan casing | Check for cleanliness and proper tightness at all anchorage points. Inspect isolators if installed for free movement. Inspect flexible gasketing between the fan and casing or duct for integrity issues such as misalignment or leakage. | Semi-annually |
| Condensate drains | Clean drain pan, flush with biocide and eliminate pockets of standing water. | Semi-annually |
| Dampers | Inspect damper actuator and linkage for proper operation by cycling fully opened to fully closed. Inspect blade gasketing if present for integrity and flexibility. Replace if damaged. | Annually |
| Filters | Inspect filter rack for integrity. Inspect local pressure differential gauge, tubing, and pitot tubes for condition. | Annually |
| Coils | Inspect coil fins for physical damage, and comb out any bent fins. Clean coils if significant dirt is present and hampering coil performance. | As-required by performance |
| Electrical connections | Tighten any loose terminal connections. | Annually |
| Outdoor grilles | Inspect and clean grilles at all exterior building penetrations | Annually |
| Sensors | Clean and calibrate sensors | Annually |