## User Documentation
Commercial Secondary Windows
Savings Calculator/
Date of last revision: |  | 2025-12-04
Version: |  | 2.0.0
Author: |  | Solarc Energy Group
Overview:
This savings calculator generates separate savings for heating, HVAC auxiliaries and cooling based on a data set developed from parametric Energy Plus runs using prototype models developed for and by BPA. Models address mid-sized offices, large offices, small hotels, large hotels, primary schools, secondary schools, small hospitals, mid-rise multifamily, and low-rise multifamily. Several user inputs act as pointers to the proper subset of data. Adjustments to the data sub-set are made via regression equations to account for differences in geography, climate, and HVAC operating hours (for offices), and average occupancy rate (for hotels). The dataset is representative of climate variations throughout United States climate zones.
Limitations:
This calculator is intended for use in building applications with existing single pane windows in the following building and representative electric and gas system types:
1) Mid-sized offices: Packaged VAV with electric reheat terminal units. |  |  | 12) Primary Schools: Distributed 4-pipe fan coil units with electric chiller and gas-fired boiler.
2) Mid-sized offices: Packaged VAV with hydronic reheat from gas-fired boilers. |  |  | 13) Secondary Schools: Single duct VAV with gas-fired hydronic reheat.
3) Large offices: Built-up single duct VAV with hydronic reheat from electric resistance boilers. |  |  | 14) Secondary Schools: Single duct VAV with electric reheat.
4) Large offices: Built-up single duct VAV with hydronic reheat from gas-fired boilers. |  |  | 15) Secondary Schools: Distributed 4-pipe fan coil units with electric chiller and electric boiler.
5) Small hotels: Packaged terminal air conditioning (PTAC) units with electric heat. |  |  | 16) Secondary Schools: Distributed 4-pipe fan coil units with electric chiller and gas-fired boiler.
6) Small hotels: Packaged terminal heat pumps (PTHPs). |  |  | 17) Small Hospital: Single duct VAV with hydronic reheat from electric resistance boiler.
7) Large hotels: Distributed 4-pipe fan coil units with electric chiller and electric boiler. |  |  | 18) Small Hospital: Single duct VAV with hydronic reheat from gas-fired boiler.
8) Large hotels: Distributed 4-pipe fan coil units with electric chiller and gas-fired boiler. |  |  | 19) Mid-rise Multifamily: Single zone fan coil units with electric hot water boiler and air-cooled chiller.
9) Primary Schools: Single duct VAV with gas-fired hydronic reheat. |  |  | 20) Mid-rise Multifamily: Single zone fan coil units with gas-fired hot water boiler and air-cooled chiller.
10) Primary Schools: Single duct VAV with electric reheat. |  |  | 21) Low-rise Multifamily: Packaged terminal air conditioning units with electric heat.
11) Primary Schools: Distributed 4-pipe fan coil units with electric chiller and electric boiler.
Instruction for use:
1) All user input and savings output iresides in one of five building type tabs: Office, Hotel, School, Hospital, or Multifamily.
2) All user input cells contain a comment that provides guidance for the user. Depending on the building type there are (13) or (14) input cells.
3) All savings output cells are calculated and highlighted in yellow.
4) The user selects the closest geograhical location from a lists designating "State" and then "Cities", that then populates the degree-day cells.
Version note:
This Beta version is populated with savings curves derived with Eplus model data for the building and system types listed above.
Input cell descriptions:
1) Information About Your Project: Input project name, address, and contact information in locations as noted.
2) Project Location (State): This is a pull-down menu inpt. User must select one of 50 states and the District of Columbia.
3) Project Location (City): This is a pull-down menu input. User must select from the list of cities that are generated by the State selection. The list of cities corresponds to the cities for which typical meteorological climate data exist. User should select the city from the list that represents the nearest city to the project location. Selection of city populates the heating and cooling degree-day entries for the project.
4) Electric Utility: This is a text entry, and is not used in the savings calculation. User should enter the name of the servicing electric utility. This information is intended to support the development of an accurate estimate of electric rate.
5) Natural Gas Utility: This is a text entry, and is not used in the savings calculation. User should enter the name of the servicing natural gas utility. If there is no natural gas utility, then enter “N/A”. This information is intended to support the development of an accurate estimate of natural gas rate.
6) Electric Rate, $/kWh: This is a numerical entry and is used to determine electric cost savings, in dollars. The user should enter the cost of electrical energy in $ per kWh. Ideally, this should not include demand charges, utility surcharges, or other charges such as meter charges. It can include taxes or local charges that are assessed on the basis of monthly energy (kWh) use. In simple terms, this entry is intended to be derived by dividing a typical total monthly billing charge for energy only, in $, by the monthly electric energy use in that bill, in kWh. Note that electric rate schedules and billings can be complicated. Commercial accounts can include charges for peak monthly demand (kW), capacity charges, power factor penalties, meter charges, and other categories of charges. In addition, some rate schedules incorporate different rates depending upon time-of-use or magnitude of use (tiered rates). Most time-of use rates charge more for energy used during the utility peak times. Most tiered rates charge less for the highest tier of use. To make the most accurate estimate of energy cost savings, it is important to account for the cost of the electrical energy that will be most affected by the installation of CSW units. This cost is often referred to as the marginal electric rates. A simple way to estimate the marginal rate would be to divide the difference in two monthly billing charges by the difference in those two months energy use. For example, (Jan $ - Dec $) / (Jan kWh – Dec kWh).
7) Natural Gas Rate, $/therm: This is a numerical entry and is used to determine natural gas cost savings, in dollars. The user should enter the average annual cost of natural gas in $ per therm. This should not include utility surcharges, or other charges such as meter charges. In simple terms, this entry is intended to be derived by dividing a typical total monthly billing charge, in $, by the monthly natural gas energy use in that bill, in therms. If gas energy units are not therms, user should convert gas rate to the equivalent cost per therm. For example, gas rate at $6.00 per MMBtu (or deca-therm) would translate to an equivalent rate of $0.60 per therm. Similar to electric rates, some natural gas rate schedules incorporate different rates depending upon time-of-use or magnitude of use (tiered rates). Most time-of use rates charge more for energy used during the winter heating season. Most tiered rates charge slightly less for the highest tier of use. To make the most accurate estimate of energy cost savings, it is important to account for the cost of the natural gas energy that will be most affected by the installation of CSW units. This cost is often referred to as the marginal rate. A simple way to estimate the most applicable marginal rate would be to divide the difference in two wintertime monthly billing charges by the difference in those two months energy use. For example, (Jan $ - Dec $) / (Jan therms – Dec therms).
8) Building Area, Sq.Ft.: This is a numerical entry and is used to determine overall energy savings percentage, reported as Energy Use Intensities (in kBtu/sq.ft.-year). It is also used to estimate overall peak cooling load reduction at an overall building level, in tons of refrigeration. It is also used in combination with the Number of floors input value, to estimate the window to wall ratio and alert the user when the CSW sq.ft. input may require verification. Building area should represent the conditioned area of all floors above grade. It is recommended to exclude basement area.
9) No. of floors: This is a numerical whole number entry representing the total number of floors that are included in the Building Area entry. It is used in the logic to to estimate the window to wall ratio and alert the user when the CSW sq.ft. input may require verification. This entry does not directly affect energy savings. For Multifamily buildings, it is used to determine whether the project is Mid-rise (greater than 3 floors) or Low-rise (3 floors or less).
10) HVAC System Type: This is a pull-down menu input variable. The list of choices in the pull-down menu varies with the building type. User must select one of the entries from the pull-down menu (listed and briefly described below). The system type selection is used in the logic to determine the appropriate set of regression curves to reference for savings estimates.
a) Packaged VAV with electric reheat: This represents packaged rooftop variable air volume systems with electric resistance reheat coils in terminal units within ductwork. This is a typical HVAC system type for mid-rise office buildings. This system type can be selected for offices only of any size.
b) Packaged VAV with hydronic reheat: This represented packaged rooftop variable air volume systems with hydronic (hot water) reheat coils in terminal units within ductwork. This is a variation of typical HVAC systems for mid-rise office buildings where a gas-fired hot water boiler is installed in the building to meet system reheat needs. This system type can be selected for offices only of any size.
c) Built-up VAV with hydronic reheat from gas-fired boilers: This represents built-up variable air volume systems where air handling units and reheat coils are served by central chillers and boilers. Reheat coils in terminal units are hydronic (hot water). This is a typical HVAC system for large office buildings. This system type can be selected for offices only of any size.
d) Built-up VAV with hydronic reheat from electric resistance boilers: This represents built-up variable air volume systems where air handling units and reheat coils are served by electric-drive chillers and gas-fired boilers. Reheat coils in terminal units are hydronic (hot water). This is a typical HVAC system for large office buildings. This system type can be selected for offices of any size.
e) Packaged Terminal Air Conditioner (PTAC): This system is common for small hotels and assumes electric resistance heat. It can be selected for hotels only of any size, or low-rise multifamily.
f) Packaged Terminal Heat Pump (PTHP): This system is common for small hotels, or motels. Heating fuel is electricity via electric-drive heat pumps. It can be selected for hotels only of any size.
g) Distributed 4-pipe fan coil units (FCUs) with electric chiller and electric boiler: This system type assumes a 4-pipe hydronic distribution system serving distributed fan coil units from a central plant with electric-drive chiller and electric resistance boiler. It can be selected for hotels, schools of any size, or mid-rise multifamily.
h) Distributed 4-pipe fan coil units (FCUs) with electric chiller and gas-fired boiler: This system type assumes a 4-pipe hydronic distribution system serving distributed fan coil units from a central plant with electric-drive chiller and gas-fired boiler. It can be selected for hotels, schools of any size, or mid-rise multifamily.
i) Central Ducted VAV with gas-fired reheat: This system represented a centralized, built-up VAV system served by a 4-pipe hydronic systems for heating and cooling. A central plant with electric-drive chiller and gas-fired boiler provides the hydronic cooling and heat. It can be selected for schools or hospitals of any size.
j) Central Ducted VAV with electric resistance reheat: This system represented a centralized, built-up VAV system served by a 4-pipe hydronic systems for heating and cooling. A central plant with electric-drive chiller and anelectric resistance boiler boiler provides the hydronic cooling and heat. It can be selected for schools or hospitals of any size.
k) Other: This selection should be made for any HVAC system types that does not fit into one of the categories listed above. Note that even if this selection is made, savings will be based on simulations that assume one of the system types listed above.
11) Dominant Heating Fuel: This is a pull-down menu input variable. User must select one of the three entries from the pull-down menu – electric, natural gas, or none. This entry will be used in the logic that determines the set of regression equations to be used to estimate heating savings. For hotels and lowrise multifamily, this entry is overridden to electric if the system type chosen is PTAC or PTHP. For offices, this entry is overridden to electric if the system type chosen is Packaged VAV with Electric Reheat. If "none" is selected, savings for heating will be zero.
12) Cooling Installed?: This is a pull-down menu input variable. User must select either "yes" or "no". If "no" is selected, cooling savings for will be adjusted to reflect HVAC auxiliary savings only.
13) Tpe of Existing Window: This is a pull-down menu inpt. User must select one of the two entries from the pull-down menu - single or double. Single represents windows wth single pane clear glass (U-value of 1.04 Btu/hr-SF-F and solar heat gain coefficient (SHGC) of 0.73). Double represents windows with double pane clear glass (U-value of 0.57 Btu/hr-SF-F and SHGC of 0.63).
14) Type of CSW Analyzed: This is a pull-down menu input that is dependent upon the type of existing window selected. User must select one of the two entries from the pull-down menu - single or double. Note that for double pane existing windows, the only selection in single. Single represents single pane CSW product lines, and is the most common type of CSW product in the current market. Savings reported in this calculator for single pane CSW (in combination with single pane primary window) assume that improved window U-value of 0.47 Btu/hr-SF-F and improved window solar heat gain coeefiecient (SHGC) of 0.57. Savings reported in this calculator for single pane CSW (in combination with double pane primary window) assume that improved window U-value of 0.40 Btu/hr-SF-F and improved window solar heat gain coefiecient (SHGC) of 0.47. Double represents double pane CSW product lines. Savings reported in this calculator for double pane CSW (in combination with a single pane primary window) assume that improved window U-value of 0.37 Btu/hr-SF-F and improved window solar heat gain coeefiecient (SHGC) of 0.32. This entry will be used in the logic that determines the set of regression equations to be used to estimate savings.
15) Sq.Ft. of CSW Installed: This is a numerical entry representing the total area, in sq.ft. of CSW units being considered for installation. The input is not limited to a minimum or a maximum value. However, if a value less than zero is input, negative savings will be reported. This is not a relevant answer, therefore a negative number should not be input. If an excessively large number is input that results in an estimated window to wall ratio greater than 50%, a user alert will be generated, “Warning: Sq.Ft of CSW Installed Appears Larger than Practical for this Building Size”.
Special input cells:
For offices only: Annual Operating Hours: This is a numerical whole number entry with limits defined. Minimum entry is 1986 hours per year. Maximum entry is 8760 hours per year, representing continuous operation. Entry is the number of HVAC operating hours per year, averaged for the entire building.
For hotels only: Ave. Occupancy Rate: This is a percentage entry that represents that average annual occupancy rate of the hotel. It has implicit limits. Any entry less than 33% will use 33% in the savings logic. Entries above 100% will use 100% in the savings logic. Entries between 33% and 100% will interpolate between minimum and maixmum savings factors.
For schools only: Building Type: This is a pull-down menu selection that allows user to select Primary or Secondary School type.
For multifamily only: Infiltration Savings: This is a pull-down menu selection that allows user to select "Included" or "Excluded". If infiltraton savings is included, then estimated savings includes a benefit associated with reduced perimeter zone infiltration. If excluded, reported savings will be adjusted to reflect savings based only on improved window U-value and SHGC.

## Office
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Large Office | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name
Project Address | Street | City, State | Zip Code
New York, NY
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 212358.9268
Annual Natural Gas Energy Savings, therms/yr |  |  | 22419.0841
Annual Energy Cost Savings, $/year |  |  | 70128.2356
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 96.9029
Savings, % and kBtu/SF-year: |  | 12.25% | 11.8668
Information About Your Building Location |  | Information About Your Building | [10 empty] | 0
|  | Building Type | Office
Project Location (State) | New_York | Building Area, Sq.Ft. | 250000 | Minimum office size limit is approximately 15,000 sq.ft. Maximum office size limit is approximately 500,000 sq.ft.
Project Location (City) | New York | No. of Floors | 10 | Mid-size offices are typically 3 floors or less in height.
Electric Utility | Con Edison | HVAC System Type | Built-up VAV with hydronic reheat | For heat pumps, adjustment of electrical heating savings is warranted. See user documentation.
Natural Gas Utility | Con Edison | Heating Fuel | Natural Gas | For packaged VAV options, make sure the fuel type is consistent with the system choice, especially for electric reheat (fuel type=electric.) | [8 empty] | SingleSingleMidOfficePVAV_ElecElectricLo
|  | Cooling Installed? | Yes | Savings includes reduction in mechanical cooling. |  | Lookup Key & Interpolation Factors | [7 empty] | Savings Factors |  |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 4885 | Annual Operating Hours | 4000 | Minimum input is 1980 hours/yr. Maximum input is 8760 hours/yr. |  | Base | CSW Type | Size | Building Type | HVAC System Type | Fuel | Hours | LU Conc | H, kWh | C, kWh | H, therms | EUI | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 1133 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 | Hi | Single | Single | Large | Office | VAV | Natural Gas | 8760 | SingleSingleLargeOfficeVAVNatural Gas8760 | 0 | 12.2721 | 1.442 | 147.5656 | 1 | 96.9029 | 0 | 557.581 | 0 | Baseline
|  | Information About Your Proposed CSW Project |  |  | Lo | Single | Single | Large | Office | VAV | Natural Gas | 2912 | SingleSingleLargeOfficeVAVNatural Gas2912 | 0 | 5.8916 | 0.58852 | 85.3228 |  | 85.0361 | 11.8668 | 510.1056 | 47.4754 | CSW
Information About Your Building |  | Type of CSW Analyzed | Single | Do not select double pane secondary windows added to double pane primary windows. | [14 empty] | % | 0.12246 |  | 0.085145
Electric Rate, $/kWh | 0.25 | Sq.ft. of CSW Installed | 30000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0.76 | Est. Window Wall Ratio | 0.31623
Savings Output
Heating, kWh/SFCSW | 0 | Electric Savings, kWh/yr | 212358.9268
Cooling & Fans, kWh/SFCSW | 7.0786
Heating, therms/SFcSW | 0.7473 | Gas Savings, therms/yr | 22419.0841
Electric Cost Savings, $/yr | 53089.7317 | Total Savings, kBtu/SF-yr | 11.8668
Gas Cost Savings, $/yr | 17038.5039 | Total Savings, $/yr | 70128.2356
Annual Percentage Total Energy Savings |  |  | 12.25%
Percentage HVAC Downsize |  |  | 8.515%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of U.S. states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry including basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing electric utility.
Note on F21: Insert predominant heating fuel. For electric resistance reheat systems, select "electric."
Note on F22: Select "No" if there is no cooling system installed.
Note on F23: Enter average annual operating hours for HVAC system. Include hours that system operates at night or in other unoccupied periods.
Note on F24: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Hotel
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Large Hotel | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Royal Hawaiian Example
Project Address | Street | City, State | Zip Code
Honolulu HI
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 503417.804
Annual Natural Gas Energy Savings, therms/yr |  |  | 0
Annual Energy Cost Savings, $/year |  |  | 191298.7655
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 101.9145
Savings, % and kBtu/SF-year |  | 14.05% | 14.318
Information About Your Building Location |  | Information About Your Building | [11 empty] | 0
|  | Building Type | Large Hotel
Project Location (State) | Colorado | Building Area, Sq.Ft. | 120000 | Minimum small hotel size limit is approximately 15,000 sq.ft. Maximum size limit is approximately 250,000 sq.ft.
Project Location (City) | Denver | No. of Floors | 10
Electric Utility | Hawaiian Electric | HVAC System Type | Fan Coil Unit | PTAC or PTHP choice will default to Small Hotel regardless of building area input. Fan Coil Unit or Other choice will default to large hotel regardless of building area input.
Natural Gas Utility | N/A | Dominant Heating Fuel | Electric | User can select either Electric or Natural Gas as fuel type. Select None if the building does not have installed heating.
|  | Cooling Installed? | Yes | Savings includes reduction in mechanical cooling. |  | Lookup Key & Interpolation Factors | [8 empty] | Savings Factors |  |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 5655 | Ave. Occupancy Rate | 100% | Typical occupancy rate is between 50% to 100%. For savings estimates, occupancy rates between 33% and 100% are used. |  | Base | CSW Type | Size | Building Type | HVAC System Type | Fuel | PTHP HDD | Occ | LU Conc | H, kWh | C, kWh | H, therms | EUI | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 923 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 | High | Single | Double | Large | Hotel | FCU | Electric |  | 100 | SingleDoubleLargeHotelFCUElectric100 | 13.0421 | 7.0946 | 0 | 101.9145 | 1 | 101.9145 | 0 | 210.9969 | 0 | Baseline
|  | Information About Your Proposed CSW Project |  |  | Low | Single | Double | Large | Hotel | FCU | Electric |  | 33 | SingleDoubleLargeHotelFCUElectric33 | 9.9332 | 5.5613 | 0 | 97.4639 |  | 87.5965 | 14.318 | 187.7851 | 23.2118 | CSW
Information About Your Building |  | Type of CSW Analyzed | Double | Do not select double pane secondary windows added to double pane primary windows. | [15 empty] | % | 0.14049 |  | 0.11001
Electric Rate, $/kWh | 0.38 | Sq.ft. of CSW Installed | 25000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0 | Est. Window Wall Ratio | 0.38036
Savings Output
Heating, kWh/SFCSW | 13.0421 | Electric Savings, kWh/yr | 503417.804
Cooling & Fans, kWh/SFCSW | 7.0946
Heating, therms/SFCSW | 0 | Gas Savings, therms/yr | 0
Electric Cost Savings, $/yr | 191298.7655 | Total Savings, kBtu/SF-yr | 14.318
Gas Cost Savings, $/yr | 0 | Total Savings, $/yr | 191298.7655
Annual Percentage Total Energy Savings |  |  | 14.05%
Percentage HVAC Downsize |  |  | 11%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of U.S states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance or heat pump systems, select "electric."
Note on F22: For electric resistance heating only systems, select "No."
Note on F23: Enter average annual occupancy rate.
Note on F24: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## School
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Secondary School | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | 300000 SF High School Example
Project Address | Street | City, State | Zip Code
Salt Lake City UT
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 65007.9251
Annual Natural Gas Energy Savings, therms/yr |  |  | 7730.5222
Annual Energy Cost Savings, $/year |  |  | 7888.7095
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 82.2746
Savings, % and kBtu/SF-year |  | 4.031% | 3.3164
Information About Your Building Location |  | Information About Your Building | [9 empty] | 0
|  | Building Type | Secondary School | Select school type - primary (elementary) or secondary (middle or high school).
Project Location (State) | Utah | Building Area, Sq.Ft. | 300000 | Minimum school size limit is approximately 25,000 sq.ft. Maximum size limit is approximately 350,000 sq.ft.
Project Location (City) | Salt Lake City | No. of Floors | 2
Electric Utility | Rocky Mountain Power | HVAC System Type | Central Ducted VAV | For heat pumps, adjustment of electrical heating savings is warranted. See user documentation.
Natural Gas Utility | Enbridge Gas | Dominant Heating Fuel | Natural Gas
|  | Cooling Installed? | Yes |  | Lookup Key | [7 empty] | Savings Factors |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 5350 | Type of Existing Window | Double pane | U-assembly = 0.57 Btu/hr-SF-F; SHGC = 0.63 | Base | CSW Type | Building Type | HVAC System Type | Fuel | Location | Occ | LU Conc | H, kWh | C, kWh | H, therms | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 1118 |  |  |  | Double | Single | SS | VAV | Natural Gas |  |  | DoubleSingleSSVAVNatural Gas | 0 | 4.3339 | 0.51537 | 1 | 82.2746 | 0 | 431.4394 | 0 | Baseline
|  | Information About Your Proposed CSW Project | [14 empty] | 78.9582 | 3.3164 | 411.8439 | 19.5955 | CSW
Information About Your Building |  | Type of CSW Analyzed | Single | Double pane secondary windows are a valid entry only for buildings with existing single pane windows. | [12 empty] | % | 0.040309 |  | 0.045419
Electric Rate, $/kWh | 0.05 | Sq.ft. of CSW Installed | 15000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0.6 | Est. Window Wall Ratio | 0.32275
Savings Output
Heating, kWh/SFCSW | 0 | Electric Savings, kWh/yr | 65007.9251
Cooling & Fans, kWh/SFCSW | 4.3339
Heating, therms/SFCSW | 0.51537 | Gas Savings, therms/yr | 7730.5222
Electric Cost Savings, $/yr | 3250.3963 | Total Savings, kBtu/SF-yr | 3.3164
Gas Cost Savings, $/yr | 4638.3133 | Total Savings, $/yr | 7888.7095
Annual Percentage Total Energy Savings |  |  | 4.031%
Percentage HVAC Downsize |  |  | 4.542%
Note on C4: Identify individual project name and/or calculation run.
Note on F17: Select school type.
Note on C18: Select appropriate state from list of Pacific Northwest states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance reheat systems, select "electric."
Note on F23: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Hospital
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Hospital | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Small Hospital Example
Project Address | Street | City, State | Zip Code
Walla Walla WA
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 188469.3571
Annual Natural Gas Energy Savings, therms/yr |  |  | 18037.5776
Annual Energy Cost Savings, $/year |  |  | 27483.0092
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 230.1992
Savings, % and kBtu/SF-year |  | 5.062% | 11.6524
Information About Your Building Location |  | Information About Your Building
|  | Building Type | Hospital
Project Location (State) | Washington | Building Area, Sq.Ft. | 210000 | Minimum size limit for small hospital is approximately 30,000 sq.ft. Maximum size limit is approximately 300,000 sq.ft.
Project Location (City) | Walla Walla | No. of Floors | 4
Electric Utility | Pacific Power | HVAC System Type | Central Ducted VAV | For heat pumps, adjustment of electrical heating savings is warranted. See user documentation.
Natural Gas Utility | NWN | Dominant Heating Fuel | Natural Gas
|  | Cooling Installed? | Yes |  | Lookup Key | [7 empty] | Savings Factors |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 4836 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 | Base | CSW Type | Building Type | HVAC System Type | Fuel | Location | Occ | LU Conc | H, kWh | C, kWh | H, therms | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 839 |  |  |  | Single | Double | Hosp | VAV | Natural Gas |  |  | SingleDoubleHospVAVNatural Gas | 0 | 15.7058 | 1.5031 | 1 | 230.1992 | 0 | 365.1315 | 0 | Baseline
|  | Information About Your ProposedCSW Project | [14 empty] | 218.5468 | 11.6524 | 340.8423 | 24.2892 | CSW
Information About Your Building |  | Type of CSW Analyzed | Double | Double pane secondary windows are a valid entry only for buildings with existing single pane windows. | [12 empty] | % | 0.050619 |  | 0.066522
Electric Rate, $/kWh | 0.075 | Sq.ft. of CSW Installed | 12000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0.74 | Est. Window Wall Ratio | 0.21822
Savings Output
Heating, kWh/SFCSW | 0 | Electric Savings, kWh/yr | 188469.3571
Cooling & Fans, kWh/SFCSW | 15.7058
Heating, therms/SFCSW | 1.5031 | Gas Savings, therms/yr | 18037.5776
Electric Cost Savings, $/yr | 14135.2018 | Total Savings, kBtu/SF-yr | 11.6524
Gas Cost Savings, $/yr | 13347.8074 | Total Savings, $/yr | 27483.0092
Annual Percentage Total Energy Savings |  |  | 5.062%
Percentage HVAC Downsize |  |  | 6.652%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of Pacific Northwest states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance reheat systems, select "electric."
Note on F23: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Multi-family
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Low-rise Multifamily | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Low Rise Apartment Example
Project Address | Street | City, State | Zip Code
Raliegh NC
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 81052.5708
Annual Natural Gas Energy Savings, therms/yr |  |  | 0
Annual Energy Cost Savings, $/year |  |  | 13778.937
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 12.1613
Savings, % and kBtu/SF-year |  | 27.17% | 13.8316
Information About Your Building Location |  | Information About Your Building | [9 empty] | 0
|  | Building Type | Low-rise Multifamily
Project Location (State) | Colorado | Building Area, Sq.Ft. | 20000 | Minimum multi-family size limit is approximately 10,000 sq.ft. Maximum size limit is approximately 150,000 sq.ft.
Project Location (City) | Denver | No. of Floors | 2 | Mid-size multi-family buildings are designated for all buildings 4 floors and above.
Electric Utility | Duke Energy | HVAC System Type | Other | Savings estimated for Low-rise assume Packaged terminal air conditioner (PTAC) system. Savings for Mid-rise assume Fan coil unit (FCU) system.")
Natural Gas Utility | N/A | Dominant Heating Fuel | Electric | [13 empty] | Heat | Cool
|  | Cooling Installed? | Yes | Savings includes reduction in mechanical cooling. |  | Lookup Key & Interpolation Factors | [6 empty] | Savings Factors |  |  |  | Infil | Infil | Clg | Graphics Drivers
Location HDD (Base 65) | 5655 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 |  | Base | CSW Type | Size | Building Type | HVAC System Type | Fuel | LU Conc | H, kWh | C, kWh | H, therms | EUI | Factor | Factor | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 923 | Infiltration Savings | Included | Savings includes contribution of reduced air leakage.
[5 empty] | High | Single | Double | Low | MF | PTAC | Electric | SingleDoubleLowMFPTACElectric | 12.1613 | 8.1018 | 0 | 50.9105 | 1 | 1 | 1 | 50.9105 | 0 | 36.287 | 0 | Baseline
|  | Information About Your Proposed CSW Project | [17 empty] | 37.0789 | 13.8316 | 21.5476 | 14.7394 | CSW
Information About Your Building |  | Type of CSW Analyzed | Double | Do not select double pane secondary windows added to double pane primary windows. | [15 empty] | % | 0.27168 |  | 0.40619
Electric Rate, $/kWh | 0.17 | Sq.ft. of CSW Installed | 4000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such that WWR is 0.25.
Natural Gas Rate, $/therm | 0 | Est. Window Wall Ratio | 0.33333
Savings Output
Heating, kWh/SFCSW | 12.1613 | Electric Savings, kWh/yr | 81052.5708
Cooling & Fans, kWh/SFCSW | 8.1018
Heating, therms/SFCSW | 0 | Gas Savings, therms/yr | 0
Electric Cost Savings, $/yr | 13778.937 | Total Savings, kBtu/SF-yr | 13.8316
Gas Cost Savings, $/yr | 0 | Total Savings, $/yr | 13778.937
Annual Percentage Total Energy Savings |  |  | 27.17%
200
Percentage HVAC Downsize |  |  | 40.62%
| 36.3 | 20000 | 550.9642
| 21.55 | 20000 | 928.0742
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of U.S. states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance heat including PTAC systems, select "electric."
Note on F23: Enter the dominent type of existing window.
Note on F24: Indicate whether savings due to reduced infiltration is to be included.
Note on F27: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C28: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F28: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C29: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Savings Lookup (hidden)
Savings Look-up Tables (using Regression Equations with HDD/CDD as independent variables)
[9 empty] | Savings |  |  |  |  | EUI |  |  |  | Loads | Loads
[9 empty] | Electric Savings, kWh/SF |  | Gas Savings, therms/SF |  | Regression Done | Base EUI | CSW EUI |  | Regression Done | Baseline Peak Cooling | Clg Load Reduced | Htg Load Reduced | Baseline Peak Cooling | Base Clg Load | CSW Ld Red | CSW Ld Red | CWS Clg Load | Regression done | Infil Savings Reduction Factors |  | Cool Adjust
Base | CSW Type | Building Size | Building Type | HVAC System Type | Fuel Type | PTHP | Hours | Look-up Conc | Heat | Cooling + Aux | Heat |  |  | kBtu/SF-yr |  |  |  | Btuh/SF | Btuh/SF | Btuh/SF | Btuh | Tons | Btuh | Tons | Tons |  | Heat | Cool
Single | Single | Mid | Office | PVAV_Elec | Electric |  | 2080 | SingleSingleMidOfficePVAV_ElecElectric2080 | 7.6688 | 3.0292 | 0 |  | Y | 51.0964 | 39.2297 | 23.22% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203 | 0.14064
Single | Single | Mid | Office | PVAV_Elec | Electric |  | 2912 | SingleSingleMidOfficePVAV_ElecElectric2912 | 10.9155 | 4.986 | 0 |  | Y | 60.166 | 48.2993 | 19.72% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203 | 0.14064
Single | Single | Mid | Office | PVAV_Elec | Electric |  | 8760 | SingleSingleMidOfficePVAV_ElecElectric8760 | 27.0246 | 10.4071 | 0 |  | Y | 128.5889 | 116.7222 | 9.228% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203 | 0.14064
Single | Double | Mid | Office | PVAV_Elec | Electric |  | 2080 | SingleDoubleMidOfficePVAV_ElecElectric2080 | 7.1234 | 5.3282 | 0 |  | Y | 51.0964 | 39.2297 | 23.22% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203 | 0.28512
Single | Double | Mid | Office | PVAV_Elec | Electric |  | 2912 | SingleDoubleMidOfficePVAV_ElecElectric2912 | 10.3101 | 7.9887 | 0 |  | Y | 60.166 | 48.2993 | 19.72% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203 | 0.28512
Single | Double | Mid | Office | PVAV_Elec | Electric |  | 8760 | SingleDoubleMidOfficePVAV_ElecElectric8760 | 28.3897 | 13.2929 | 0 |  | Y | 128.5889 | 116.7222 | 9.228% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203 | 0.28512
Double | Single | Mid | Office | PVAV_Elec | Electric |  | 2080 | DoubleSingleMidOfficePVAV_ElecElectric2080 | 3.4877 | 2.1054 | 0 |  | Y | 47.81 | 35.9433 | 24.82% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203 | 0.11135
Double | Single | Mid | Office | PVAV_Elec | Electric |  | 2912 | DoubleSingleMidOfficePVAV_ElecElectric2912 | 4.6262 | 3.1044 | 0 |  | Y | 55.5401 | 43.6733 | 21.37% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203 | 0.11135
Double | Single | Mid | Office | PVAV_Elec | Electric |  | 8760 | DoubleSingleMidOfficePVAV_ElecElectric8760 | 13.1367 | 5.1491 | 0 |  | Y | 115.8634 | 103.9966 | 10.24% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203 | 0.11135
Single | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2080 | SingleSingleMidOfficePVAV_GasNatural Gas2080 | 0 | 3.0292 | 0.37448 |  | Y | 57.1771 | 45.3104 | 20.75% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203 | 0.14064
Single | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2912 | SingleSingleMidOfficePVAV_GasNatural Gas2912 | 0 | 4.986 | 0.53194 |  | Y | 78.0253 | 66.1585 | 15.21% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203 | 0.14064
Single | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 8760 | SingleSingleMidOfficePVAV_GasNatural Gas8760 | 0 | 10.4071 | -2.8646 |  | Y | 156.5864 | 144.7197 | 7.578% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203 | 0.14064
Single | Double | Mid | Office | PVAV_Gas | Natural Gas |  | 2080 | SingleDoubleMidOfficePVAV_GasNatural Gas2080 | 0 | 5.3282 | 0.34688 |  | Y | 57.1771 | 45.3104 | 20.75% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203 | 0.28512
Single | Double | Mid | Office | PVAV_Gas | Natural Gas |  | 2912 | SingleDoubleMidOfficePVAV_GasNatural Gas2912 | 0 | 7.9887 | 0.50268 |  | Y | 78.0253 | 66.1585 | 15.21% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203 | 0.28512
Single | Double | Mid | Office | PVAV_Gas | Natural Gas |  | 8760 | SingleDoubleMidOfficePVAV_GasNatural Gas8760 | 0 | 13.2929 | 1.3828 |  | Y | 156.5864 | 144.7197 | 7.578% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203 | 0.28512
Double | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2080 | DoubleSingleMidOfficePVAV_GasNatural Gas2080 | 0 | 2.1054 | 0.16957 |  | Y | 47.8279 | 35.9612 | 24.81% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203 | 0.11135
Double | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2912 | DoubleSingleMidOfficePVAV_GasNatural Gas2912 | 0 | 3.1044 | 0.2249 |  | Y | 55.3919 | 43.5252 | 21.42% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203 | 0.11135
Double | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 8760 | DoubleSingleMidOfficePVAV_GasNatural Gas8760 | 0 | 5.1491 | 0.63825 |  | Y | 115.8848 | 104.0181 | 10.24% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203 | 0.11135
Single | Single | Large | Office | VAV | Electric |  | 2080 | SingleSingleLargeOfficeVAVElectric2080 | 8.3768 | 3.5966 | 0 |  | Y | 52.0782 | 40.2114 | 22.79% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996 | 0.085145
Single | Single | Large | Office | VAV | Electric |  | 2912 | SingleSingleLargeOfficeVAVElectric2912 | 12.0673 | 5.8916 | 0 |  | Y | 79.0511 | 67.1843 | 15.01% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996 | 0.085145
Single | Single | Large | Office | VAV | Electric |  | 8760 | SingleSingleLargeOfficeVAVElectric8760 | 29.5821 | 12.2721 | 0 |  | Y | 137.2754 | 125.4086 | 8.644% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996 | 0.085145
Single | Double | Large | Office | VAV | Electric |  | 2080 | SingleDoubleLargeOfficeVAVElectric2080 | 7.7938 | 6.3007 | 0 |  | Y | 52.0782 | 40.2114 | 22.79% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996 | 0.25972
Single | Double | Large | Office | VAV | Electric |  | 2912 | SingleDoubleLargeOfficeVAVElectric2912 | 11.2347 | 9.421 | 0 |  | Y | 79.0511 | 67.1843 | 15.01% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996 | 0.25972
Single | Double | Large | Office | VAV | Electric |  | 8760 | SingleDoubleLargeOfficeVAVElectric8760 | 31.2095 | 15.6912 | 0 |  | Y | 137.2754 | 125.4086 | 8.644% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996 | 0.25972
Double | Single | Large | Office | VAV | Electric |  | 2080 | DoubleSingleLargeOfficeVAVElectric2080 | 3.8329 | 2.4676 | 0 |  | Y | 106.8943 | 95.0275 | 11.1% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996 | 0.10324
Double | Single | Large | Office | VAV | Electric |  | 2912 | DoubleSingleLargeOfficeVAVElectric2912 | 5.0846 | 3.6288 | 0 |  | Y | 73.4438 | 61.577 | 16.16% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996 | 0.10324
Double | Single | Large | Office | VAV | Electric |  | 8760 | DoubleSingleLargeOfficeVAVElectric8760 | 14.3964 | 6.0331 | 0 |  | Y | 123.8742 | 112.0074 | 9.58% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996 | 0.10324
Single | Single | Large | Office | VAV | Natural Gas |  | 2080 | SingleSingleLargeOfficeVAVNatural Gas2080 | 0 | 3.5966 | 0.40825 |  | Y | 53.3199 | 41.4531 | 22.26% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996 | 0.085145
Single | Single | Large | Office | VAV | Natural Gas |  | 2912 | SingleSingleLargeOfficeVAVNatural Gas2912 | 0 | 5.8916 | 0.58852 |  | Y | 85.3228 | 73.4561 | 13.91% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996 | 0.085145
Single | Single | Large | Office | VAV | Natural Gas |  | 8760 | SingleSingleLargeOfficeVAVNatural Gas8760 | 0 | 12.2721 | 1.442 |  | Y | 147.5656 | 135.6989 | 8.042% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996 | 0.085145
Single | Double | Large | Office | VAV | Natural Gas |  | 2080 | SingleDoubleLargeOfficeVAVNatural Gas2080 | 0 | 6.3007 | 0.37827 |  | Y | 53.3199 | 41.4531 | 22.26% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996 | 0.25972
Single | Double | Large | Office | VAV | Natural Gas |  | 2912 | SingleDoubleLargeOfficeVAVNatural Gas2912 | 0 | 9.421 | 0.54512 |  | Y | 85.3228 | 73.4561 | 13.91% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996 | 0.25972
Single | Double | Large | Office | VAV | Natural Gas |  | 8760 | SingleDoubleLargeOfficeVAVNatural Gas8760 | 0 | 15.6912 | 1.5209 |  | Y | 147.5656 | 135.6989 | 8.042% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996 | 0.25972
Double | Single | Large | Office | VAV | Natural Gas |  | 2080 | DoubleSingleLargeOfficeVAVNatural Gas2080 | 0 | 2.4676 | 0.18581 |  | Y | 53.1479 | 41.2812 | 22.33% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996 | 0.10324
Double | Single | Large | Office | VAV | Natural Gas |  | 2912 | DoubleSingleLargeOfficeVAVNatural Gas2912 | 0 | 3.6288 | 0.24747 |  | Y | 80.12 | 68.2532 | 14.81% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996 | 0.10324
Double | Single | Large | Office | VAV | Natural Gas |  | 8760 | DoubleSingleLargeOfficeVAVNatural Gas8760 | 0 | 6.0331 | 0.70013 |  | Y | 131.0398 | 119.1731 | 9.056% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996 | 0.10324
Single | Single | Small | Hotel | PTAC | Electric |  | 33 | SingleSingleSmallHotelPTACElectric33 | 9.1235 | 2.3037 | 0 | 0.21666 | Y | 61.8933 | 47.5752 | 23.13% | Y | 19.9845 | 18.8826 |  | 2398138.5487 | 199.8449 | 472065.1808 | 39.3388 | 160.5061 | Y |  |  | #REF! | 0.19685
Single | Single | Small | Hotel | PTAC | Electric |  | 100 | SingleSingleSmallHotelPTACElectric100 | 11.2457 | 3.1747 | 0 | 0.21666 | Y | 66.4938 | 52.1758 | 21.53% | Y | 19.9845 | 18.8826 |  | 2398138.5487 | 199.8449 | 472065.1808 | 39.3388 | 160.5061 | Y |  |  | #REF! | 0.19685
Single | Double | Small | Hotel | PTAC | Electric |  | 33 | SingleDoubleSmallHotelPTACElectric33 | 8.3437 | 4.7347 | 0 | 0.21666 | Y | 61.8933 | 47.5752 | 23.13% | Y | 19.9845 | 34.6367 |  | 2398138.5487 | 199.8449 | 865918.0658 | 72.1598 | 127.685 | Y |  |  | #REF! | 0.36108
Single | Double | Small | Hotel | PTAC | Electric |  | 100 | SingleDoubleSmallHotelPTACElectric100 | 10.2838 | 6.2209 | 0 | 0.21666 | Y | 66.4938 | 52.1758 | 21.53% | Y | 19.9845 | 34.6367 |  | 2398138.5487 | 199.8449 | 865918.0658 | 72.1598 | 127.685 | Y |  |  | #REF! | 0.36108
Double | Single | Small | Hotel | PTAC | Electric |  | 33 | DoubleSingleSmallHotelPTACElectric33 | 3.4054 | 1.7595 | 0 | 0.21666 | Y | 63.2757 | 48.9576 | 22.63% | Y | 19.6789 | 12.3316 |  | 2361467.3389 | 196.7889 | 308289.854 | 25.6908 | 171.0981 | Y |  |  | #REF! | 0.13055
Double | Single | Small | Hotel | PTAC | Electric |  | 100 | DoubleSingleSmallHotelPTACElectric100 | 5.2509 | 2.1269 | 0 | 0.21666 | Y | 65.8682 | 51.5501 | 21.74% | Y | 19.6789 | 12.3316 |  | 2361467.3389 | 196.7889 | 308289.854 | 25.6908 | 171.0981 | Y |  |  | 0.21666 | 0.13055
Single | Single | Small | Hotel | PTHP | Electric | Low | 33 | SingleSingleSmallHotelPTHPElectricLow33 | 4.0312 | 2.3037 | 0 | 0.21666 | Y | 44.824 | 30.506 | 31.94% | Y | 19.9845 | 18.8826 |  | 2398138.5487 | 199.8449 | 472065.1808 | 39.3388 | 160.5061 | Y |  |  | 0.21666 | 0.19685
Single | Single | Small | Hotel | PTHP | Electric | High | 33 | SingleSingleSmallHotelPTHPElectricHigh33 | 8.855 | 2.3037 | 0 | 0.21666 | Y | 44.824 | 30.506 | 31.94% | Y | 19.9845 | 18.8826 |  | 2398138.5487 | 199.8449 | 472065.1808 | 39.3388 | 160.5061 | Y |  |  | 0.21666 | 0.19685
Single | Single | Small | Hotel | PTHP | Electric | Low | 100 | SingleSingleSmallHotelPTHPElectricLow100 | 4.961 | 3.1747 | 0 | 0.21666 | Y | 50.1506 | 35.8326 | 28.55% | Y | 19.9845 | 18.8826 |  | 2398138.5487 | 199.8449 | 472065.1808 | 39.3388 | 160.5061 | Y |  |  |  | 0.19685
Single | Single | Small | Hotel | PTHP | Electric | High | 100 | SingleSingleSmallHotelPTHPElectricHigh100 | 9.6551 | 3.1747 | 0 | 0.21666 | Y | 50.1506 | 35.8326 | 28.55% | Y | 19.9845 | 18.8826 |  | 2398138.5487 | 199.8449 | 472065.1808 | 39.3388 | 160.5061 | Y |  |  | 0.21666 | 0.19685
Single | Double | Small | Hotel | PTHP | Electric | Low | 33 | SingleDoubleSmallHotelPTHPElectricLow33 | 3.6896 | 4.7347 | 0 | 0.21666 | Y | 44.824 | 30.506 | 31.94% | Y | 19.9845 | 34.6367 |  | 2398138.5487 | 199.8449 | 865918.0658 | 72.1598 | 127.685 | Y |  |  | 0.21666 | 0.36108
Single | Double | Small | Hotel | PTHP | Electric | High | 33 | SingleDoubleSmallHotelPTHPElectricHigh33 | 8.55 | 4.7347 | 0 | 0.21666 | Y | 44.824 | 30.506 | 31.94% | Y | 19.9845 | 34.6367 |  | 2398138.5487 | 199.8449 | 865918.0658 | 72.1598 | 127.685 | Y |  |  | 0.21666 | 0.36108
Single | Double | Small | Hotel | PTHP | Electric | Low | 100 | SingleDoubleSmallHotelPTHPElectricLow100 | 4.5399 | 6.2209 | 0 | 0.21666 | Y | 50.1506 | 35.8326 | 28.55% | Y | 19.9845 | 34.6367 |  | 2398138.5487 | 199.8449 | 865918.0658 | 72.1598 | 127.685 | Y |  |  |  | 0.36108
Single | Double | Small | Hotel | PTHP | Electric | High | 100 | SingleDoubleSmallHotelPTHPElectricHigh100 | 9.3247 | 6.2209 | 0 | 0.21666 | Y | 50.1506 | 35.8326 | 28.55% | Y | 19.9845 | 34.6367 |  | 2398138.5487 | 199.8449 | 865918.0658 | 72.1598 | 127.685 | Y |  |  | 0.21666 | 0.36108
Double | Single | Small | Hotel | PTHP | Electric | Low | 33 | DoubleSingleSmallHotelPTHPElectricLow33 | 1.5089 | 1.7595 | 0 | 0.21666 | Y | 44.0404 | 29.7223 | 32.51% | Y | 19.6789 | 12.3316 |  | 2361467.3389 | 196.7889 | 308289.854 | 25.6908 | 171.0981 | Y |  |  | 0.21666 | 0.13055
Double | Single | Small | Hotel | PTHP | Electric | High | 33 | DoubleSingleSmallHotelPTHPElectricHigh33 | 3.9557 | 1.7595 | 0 | 0.21666 | Y | 44.0404 | 29.7223 | 32.51% | Y | 19.6789 | 12.3316 |  | 2361467.3389 | 196.7889 | 308289.854 | 25.6908 | 171.0981 | Y |  |  | 0.21666 | 0.13055
Double | Single | Small | Hotel | PTHP | Electric | Low | 100 | DoubleSingleSmallHotelPTHPElectricLow100 | 2.3163 | 2.1269 | 0 | 0.21666 | Y | 49.5836 | 35.2655 | 28.88% | Y | 19.6789 | 12.3316 |  | 2361467.3389 | 196.7889 | 308289.854 | 25.6908 | 171.0981 | Y |  |  |  | 0.13055
Double | Single | Small | Hotel | PTHP | Electric | High | 100 | DoubleSingleSmallHotelPTHPElectricHigh100 | 4.4765 | 2.1269 | 0 | 0.21666 | Y | 49.5836 | 35.2655 | 28.88% | Y | 19.6789 | 12.3316 |  | 2361467.3389 | 196.7889 | 308289.854 | 25.6908 | 171.0981 | Y |  |  | 0.21666 | 0.13055
Single | Single | Large | Hotel | FCU | Electric |  | 33 | SingleSingleLargeHotelFCUElectric33 | 10.35 | 2.6108 | 0 |  | Y | 97.4639 | 83.1459 | 14.69% | Y | 21.0997 | 6.8665 |  | 2531962.3677 | 210.9969 | 171662.4659 | 14.3052 | 196.6917 | Y |  |  | #REF! | 0.067798
Single | Single | Large | Hotel | FCU | Electric |  | 100 | SingleSingleLargeHotelFCUElectric100 | 13.8029 | 2.7514 | 0 |  | Y | 101.9145 | 87.5965 | 14.05% | Y | 21.0997 | 6.8665 |  | 2531962.3677 | 210.9969 | 171662.4659 | 14.3052 | 196.6917 | Y |  |  | #REF! | 0.067798
Single | Double | Large | Hotel | FCU | Electric |  | 33 | SingleDoubleLargeHotelFCUElectric33 | 9.9332 | 5.5613 | 0 |  | Y | 97.4639 | 83.1459 | 14.69% | Y | 21.0997 | 11.1417 |  | 2531962.3677 | 210.9969 | 278541.5327 | 23.2118 | 187.7851 | Y |  |  | #REF! | 0.11001
Single | Double | Large | Hotel | FCU | Electric |  | 100 | SingleDoubleLargeHotelFCUElectric100 | 13.0421 | 7.0946 | 0 |  | Y | 101.9145 | 87.5965 | 14.05% | Y | 21.0997 | 11.1417 |  | 2531962.3677 | 210.9969 | 278541.5327 | 23.2118 | 187.7851 | Y |  |  | #REF! | 0.11001
Double | Single | Large | Hotel | FCU | Electric |  | 33 | DoubleSingleLargeHotelFCUElectric33 | 3.7082 | 1.7608 | 0 |  | Y | 91.5816 | 77.2636 | 15.63% | Y | 18.2154 | 4.5534 |  | 2185848.8788 | 182.1541 | 113835.8306 | 9.4863 | 172.6678 | Y |  |  | #REF! | 0.052079
Double | Single | Large | Hotel | FCU | Electric |  | 100 | DoubleSingleLargeHotelFCUElectric100 | 5.158 | 2.0559 | 0 |  | Y | 96.1048 | 81.7867 | 14.9% | Y | 18.2154 | 4.5534 |  | 2185848.8788 | 182.1541 | 113835.8306 | 9.4863 | 172.6678 | Y |  |  | #REF! | 0.052079
Single | Single | Large | Hotel | FCU | Natural Gas |  | 33 | SingleSingleLargeHotelFCUNatural Gas33 | 0 | 2.6108 | 0.44143 |  | Y | 104.6445 | 90.3265 | 13.68% | Y | 21.0997 | 6.8665 |  | 2531962.3677 | 210.9969 | 171662.4659 | 14.3052 | 196.6917 | Y |  |  | #REF! | 0.067798
Single | Single | Large | Hotel | FCU | Natural Gas |  | 100 | SingleSingleLargeHotelFCUNatural Gas100 | 0 | 2.7514 | 0.58869 |  | Y | 109.1853 | 94.8673 | 13.11% | Y | 21.0997 | 6.8665 |  | 2531962.3677 | 210.9969 | 171662.4659 | 14.3052 | 196.6917 | Y |  |  | #REF! | 0.067798
Single | Double | Large | Hotel | FCU | Natural Gas |  | 33 | SingleDoubleLargeHotelFCUNatural Gas33 | 0 | 5.5613 | 0.42365 |  | Y | 104.6445 | 90.3265 | 13.68% | Y | 21.0997 | 11.1417 |  | 2531962.3677 | 210.9969 | 278541.5327 | 23.2118 | 187.7851 | Y |  |  | #REF! | 0.11001
Single | Double | Large | Hotel | FCU | Natural Gas |  | 100 | SingleDoubleLargeHotelFCUNatural Gas100 | 0 | 7.0946 | 0.55624 |  | Y | 109.1853 | 94.8673 | 13.11% | Y | 21.0997 | 11.1417 |  | 2531962.3677 | 210.9969 | 278541.5327 | 23.2118 | 187.7851 | Y |  |  | #REF! | 0.11001
Double | Single | Large | Hotel | FCU | Natural Gas |  | 33 | DoubleSingleLargeHotelFCUNatural Gas33 | 0 | 1.7608 | 0.15816 |  | Y | 97.7458 | 83.4278 | 14.65% | Y | 18.2154 | 4.5534 |  | 2185848.8788 | 182.1541 | 113835.8306 | 9.4863 | 172.6678 | Y |  |  | #REF! | 0.052079
Double | Single | Large | Hotel | FCU | Natural Gas |  | 100 | DoubleSingleLargeHotelFCUNatural Gas100 | 0 | 2.0559 | 0.21999 |  | Y | 101.5403 | 87.2222 | 14.1% | Y | 18.2154 | 4.5534 |  | 2185848.8788 | 182.1541 | 113835.8306 | 9.4863 | 172.6678 | Y |  |  | 0.42347 | 0.052079
Single | Single |  | PS | FCU | Electric |  |  | SingleSinglePSFCUElectric | 11.4771 | 1.2037 | 0 |  | Y | 52.7062 | 49.3898 | 6.292% | Y | 29.217 | 26.9659 |  | 8765091.5863 | 730.4243 | 404488.7166 | 33.7074 | 696.7169 | Y |  |  | 0.68905 | 0.046148
Single | Double |  | PS | FCU | Electric |  |  | SingleDoublePSFCUElectric | 10.5594 | 2.1225 | 0 |  | Y | 52.7062 | 49.3898 | 6.292% | Y | 29.0669 | 47.886 |  | 8720070.1218 | 726.6725 | 718289.5872 | 59.8575 | 666.815 | Y |  |  | 0.68905 | 0.082372
Double | Single |  | PS | FCU | Electric |  |  | DoubleSinglePSFCUElectric | 5.9767 | 1.0194 | 0 |  | Y | 49.3542 | 46.0378 | 6.72% | Y | 26.3232 | 16.8093 |  | 7896949.1354 | 658.0791 | 252138.9164 | 21.0116 | 637.0675 | Y |  |  | 0.68905 | 0.031929
Single | Single |  | PS | VAV | Electric |  |  | SingleSinglePSVAVElectric | 15.218 | 5.0873 | 0 |  | Y | 59.4106 | 56.0942 | 5.582% | Y | 29.217 | 26.9659 |  | 8765091.5863 | 730.4243 | 404488.7166 | 33.7074 | 696.7169 | Y |  |  | 0.32199 | 0.046148
Single | Double |  | PS | VAV | Electric |  |  | SingleDoublePSVAVElectric | 15.0914 | 8.1155 | 0 |  | Y | 59.4106 | 56.0942 | 5.582% | Y | 29.0669 | 47.886 |  | 8720070.1218 | 726.6725 | 718289.5872 | 59.8575 | 666.815 | Y |  |  | 0.32199 | 0.082372
Double | Single |  | PS | VAV | Electric |  |  | DoubleSinglePSVAVElectric | 11.031 | 4.1236 | 0 |  | Y | 54.822 | 51.5056 | 6.049% | Y | 26.3232 | 16.8093 |  | 7896949.1354 | 658.0791 | 252138.9164 | 21.0116 | 637.0675 | Y |  |  | 0.32199 | 0.031929
Single | Single |  | PS | FCU | Natural Gas |  |  | SingleSinglePSFCUNatural Gas | 0 | 1.2037 | 0.4895 |  | Y | 56.9136 | 53.5972 | 5.827% | Y | 29.217 | 26.9659 |  | 8765091.5863 | 730.4243 | 404488.7166 | 33.7074 | 696.7169 | Y |  |  | 0.68905 | 0.046148
Single | Double |  | PS | FCU | Natural Gas |  |  | SingleDoublePSFCUNatural Gas | 0 | 2.1225 | 0.45036 |  | Y | 56.9136 | 53.5972 | 5.827% | Y | 29.0669 | 47.886 |  | 8720070.1218 | 726.6725 | 718289.5872 | 59.8575 | 666.815 | Y |  |  | 0.68905 | 0.082372
Double | Single |  | PS | FCU | Natural Gas |  |  | DoubleSinglePSFCUNatural Gas | 0 | 1.0194 | 0.25491 |  | Y | 52.7246 | 49.4081 | 6.29% | Y | 26.3232 | 16.8093 |  | 7896949.1354 | 658.0791 | 252138.9164 | 21.0116 | 637.0675 | Y |  |  | 0.68905 | 0.031929
Single | Single |  | PS | VAV | Natural Gas |  |  | SingleSinglePSVAVNatural Gas | 0 | 5.0873 | 0.64905 |  | Y | 64.9834 | 61.6669 | 5.103% | Y | 29.217 | 26.9659 |  | 8765091.5863 | 730.4243 | 404488.7166 | 33.7074 | 696.7169 | Y |  |  | 0.32199 | 0.046148
Single | Double |  | PS | VAV | Natural Gas |  |  | SingleDoublePSVAVNatural Gas | 0 | 8.1155 | 0.64365 |  | Y | 64.9834 | 61.6669 | 5.103% | Y | 29.0669 | 47.886 |  | 8720070.1218 | 726.6725 | 718289.5872 | 59.8575 | 666.815 | Y |  |  | 0.32199 | 0.082372
Double | Single |  | PS | VAV | Natural Gas |  |  | DoubleSinglePSVAVNatural Gas | 0 | 4.1236 | 0.47047 |  | Y | 59.5943 | 56.2779 | 5.565% | Y | 26.3232 | 16.8093 |  | 7896949.1354 | 658.0791 | 252138.9164 | 21.0116 | 637.0675 | Y |  |  | 0.32199 | 0.031929
Single | Single |  | SS | FCU | Electric |  |  | SingleSingleSSFCUElectric | 12.4996 | 1.2874 | 0 |  | Y | 74.5873 | 71.2709 | 4.446% | Y | 19.157 | 24.776 |  | 5747093.1089 | 478.9244 | 371639.4046 | 30.97 | 447.9545 | Y |  |  | 0.68905 | 0.064666
Single | Double |  | SS | FCU | Electric |  |  | SingleDoubleSSFCUElectric | 11.5008 | 2.413 | 0 |  | Y | 74.5873 | 71.2709 | 4.446% | Y | 19.0129 | 45.7793 |  | 5703860.5029 | 475.3217 | 686689.1126 | 57.2241 | 418.0976 | Y |  |  | 0.68905 | 0.12039
Double | Single |  | SS | FCU | Electric |  |  | DoubleSingleSSFCUElectric | 6.4473 | 1.0904 | 0 |  | Y | 70.2601 | 66.9437 | 4.72% | Y | 17.2576 | 15.6764 |  | 5177273.1197 | 431.4394 | 235146.1721 | 19.5955 | 411.8439 | Y |  |  | 0.68905 | 0.045419
Single | Single |  | SS | VAV | Electric |  |  | SingleSingleSSVAVElectric | 16.9528 | 5.3603 | 0 |  | Y | 78.3585 | 75.042 | 4.232% | Y | 19.157 | 24.776 |  | 5747093.1089 | 478.9244 | 371639.4046 | 30.97 | 447.9545 | Y |  |  | 0.32199 | 0.064666
Single | Double |  | SS | VAV | Electric |  |  | SingleDoubleSSVAVElectric | 15.6129 | 9.1059 | 0 |  | Y | 78.3585 | 75.042 | 4.232% | Y | 19.0129 | 45.7793 |  | 5703860.5029 | 475.3217 | 686689.1126 | 57.2241 | 418.0976 | Y |  |  | 0.32199 | 0.12039
Double | Single |  | SS | VAV | Electric |  |  | DoubleSingleSSVAVElectric | 12.0936 | 4.3339 | 0 |  | Y | 73.7863 | 70.4699 | 4.495% | Y | 17.2576 | 15.6764 |  | 5177273.1197 | 431.4394 | 235146.1721 | 19.5955 | 411.8439 | Y |  |  | 0.32199 | 0.045419
Single | Single |  | SS | FCU | Natural Gas |  |  | SingleSingleSSFCUNatural Gas | 0 | 1.2874 | 0.53311 |  | Y | 82.1113 | 78.7948 | 4.039% | Y | 19.157 | 24.776 |  | 5747093.1089 | 478.9244 | 371639.4046 | 30.97 | 447.9545 | Y |  |  | 0.68905 | 0.064666
Single | Double |  | SS | FCU | Natural Gas |  |  | SingleDoubleSSFCUNatural Gas | 0 | 2.413 | 0.49051 |  | Y | 82.1113 | 78.7948 | 4.039% | Y | 19.0129 | 45.7793 |  | 5703860.5029 | 475.3217 | 686689.1126 | 57.2241 | 418.0976 | Y |  |  | 0.68905 | 0.12039
Double | Single |  | SS | FCU | Natural Gas |  |  | DoubleSingleSSFCUNatural Gas | 0 | 1.0904 | 0.27498 |  | Y | 77.0938 | 73.7774 | 4.302% | Y | 17.2576 | 15.6764 |  | 5177273.1197 | 431.4394 | 235146.1721 | 19.5955 | 411.8439 | Y |  |  | 0.68905 | 0.045419
Single | Single |  | SS | VAV | Natural Gas |  |  | SingleSingleSSVAVNatural Gas | 0 | 5.3603 | 0.72304 |  | Y | 87.1139 | 83.7975 | 3.807% | Y | 19.157 | 24.776 |  | 5747093.1089 | 478.9244 | 371639.4046 | 30.97 | 447.9545 | Y |  |  | 0.32199 | 0.064666
Single | Double |  | SS | VAV | Natural Gas |  |  | SingleDoubleSSVAVNatural Gas | 0 | 9.1059 | 0.66589 |  | Y | 87.1139 | 83.7975 | 3.807% | Y | 19.0129 | 45.7793 |  | 5703860.5029 | 475.3217 | 686689.1126 | 57.2241 | 418.0976 | Y |  |  | 0.32199 | 0.12039
Double | Single |  | SS | VAV | Natural Gas |  |  | DoubleSingleSSVAVNatural Gas | 0 | 4.3339 | 0.51537 |  | Y | 82.2746 | 78.9582 | 4.031% | Y | 17.2576 | 15.6764 |  | 5177273.1197 | 431.4394 | 235146.1721 | 19.5955 | 411.8439 | Y |  |  | 0.32199 | 0.045419
Single | Single |  | Hosp | VAV | Electric |  |  | SingleSingleHospVAVElectric | 28.8332 | 12.3824 | 0 |  | Y | 204.4148 | 192.7624 | 5.7% | Y | 20.8647 | 14.063 |  | 4381577.776 | 365.1315 | 168756.2748 | 14.063 | 351.0685 | Y |  |  | 0.57542 | 0.038515
Single | Double |  | Hosp | VAV | Electric |  |  | SingleDoubleHospVAVElectric | 34.0114 | 15.7058 | 0 |  | Y | 204.4148 | 192.7624 | 5.7% | Y | 20.8647 | 24.2892 |  | 4381577.776 | 365.1315 | 291470.6327 | 24.2892 | 340.8423 | Y |  |  | 0.57542 | 0.066522
Double | Single |  | Hosp | VAV | Electric |  |  | DoubleSingleHospVAVElectric | 17.0499 | 6.9358 | 0 |  | Y | 204.4148 | 192.7624 | 5.7% | Y | 22.101 | 8.2079 |  | 4641216.1172 | 386.768 | 98494.6427 | 8.2079 | 378.5601 | Y |  |  | 0.57542 | 0.021222
Single | Single |  | Hosp | VAV | Natural Gas |  |  | SingleSingleHospVAVNatural Gas | 0 | 12.3824 | 1.2603 |  | Y | 230.1992 | 218.5468 | 5.062% | Y | 20.8647 | 14.063 |  | 4381577.776 | 365.1315 | 168756.2748 | 14.063 | 351.0685 | Y |  |  | 0.57542 | 0.038515
Single | Double |  | Hosp | VAV | Natural Gas |  |  | SingleDoubleHospVAVNatural Gas | 0 | 15.7058 | 1.5031 |  | Y | 230.1992 | 218.5468 | 5.062% | Y | 20.8647 | 24.2892 |  | 4381577.776 | 365.1315 | 291470.6327 | 24.2892 | 340.8423 | Y |  |  | 0.57542 | 0.066522
Double | Single |  | Hosp | VAV | Natural Gas |  |  | DoubleSingleHospVAVNatural Gas | 0 | 6.9358 | 0.73653 |  | Y | 230.1992 | 218.5468 | 5.062% | Y | 22.101 | 8.2079 |  | 4641216.1172 | 386.768 | 98494.6427 | 8.2079 | 378.5601 | Y |  |  | 0.57542 | 0.021222
Single | Single | Low | MF | PTAC | Electric |  |  | SingleSingleLowMFPTACElectric | 15.326 | 4.3072 | 0 |  | Y | 55.8192 | 41.9876 | 24.78% | Y | 21.7722 | 22.9489 |  | 435444.1464 | 36.287 | 91795.7863 | 7.6496 | 28.6374 | Y | 0.79517 | 0.93262 | 0.39311 | 0.21081
Single | Double | Low | MF | PTAC | Electric |  |  | SingleDoubleLowMFPTACElectric | 12.1613 | 8.1018 | 0 |  | Y | 50.9105 | 37.0789 | 27.17% | Y | 21.7722 | 44.2182 |  | 435444.1464 | 36.287 | 176872.6381 | 14.7394 | 21.5476 | Y | 0.79517 | 0.93262 | 0.39311 | 0.40619
Double | Single | Low | MF | PTAC | Electric |  |  | DoubleSingleLowMFPTACElectric | 6.9182 | 2.895 | 0 |  | Y | 44.2378 | 30.4061 | 31.27% | Y | 18.161 | 16.1982 |  | 363220.8659 | 30.2684 | 64792.9474 | 5.3994 | 24.869 | Y | 0.79517 | 0.93262 | 0.39311 | 0.17838
Single | Single | Mid | MF | FCU | Electric |  |  | SingleSingleMidMFFCUElectric | 13.6381 | 3.817 | 0 |  | Y | 46.8559 | 33.0243 | 29.52% | Y | 12.6739 | 21.3751 |  | 253478.2244 | 21.1232 | 85500.3481 | 7.125 | 13.9982 | Y | 0.79517 | 0.93262 | 0.64962 | 0.33731
Single | Double | Mid | MF | FCU | Electric |  |  | SingleDoubleMidMFFCUElectric | 10.8339 | 7.5989 | 0 |  | Y | 46.8559 | 33.0243 | 29.52% | Y | 12.6739 | 42.0337 |  | 253478.2244 | 21.1232 | 168134.934 | 14.0112 | 7.1119 | Y | 0.79517 | 0.93262 | 0.64962 | 0.66331
Double | Single | Mid | MF | FCU | Electric |  |  | DoubleSingleMidMFFCUElectric | 5.6692 | 2.547 | 0 |  | Y | 42.9122 | 29.0806 | 32.23% | Y | 10.6708 | 10.9397 |  | 213415.3498 | 17.7846 | 43758.7251 | 3.6466 | 14.1381 | Y | 0.79517 | 0.93262 | 0.64962 | 0.20504
Single | Single | Mid | MF | FCU | Natural Gas |  |  | SingleSingleMidMFFCUNatural Gas | 0 | 3.817 | 0.58166 |  | Y | 51.3364 | 37.5048 | 26.94% | Y | 12.6739 | 21.3751 |  | 253478.2244 | 21.1232 | 85500.3481 | 7.125 | 13.9982 | Y | 0.79517 | 0.93262 | 0.64962 | 0.33731
Single | Double | Mid | MF | FCU | Natural Gas |  |  | SingleDoubleMidMFFCUNatural Gas | 0 | 7.5989 | 0.46207 |  | Y | 51.3364 | 37.5048 | 26.94% | Y | 12.6739 | 42.0337 |  | 253478.2244 | 21.1232 | 168134.934 | 14.0112 | 7.1119 | Y | 0.79517 | 0.93262 | 0.64962 | 0.66331
Double | Single | Mid | MF | FCU | Natural Gas |  |  | DoubleSingleMidMFFCUNatural Gas | 0 | 2.547 | 0.24179 |  | Y | 46.3752 | 32.5436 | 29.83% | Y | 10.6708 | 10.9397 |  | 213415.3498 | 17.7846 | 43758.7251 | 3.6466 | 14.1381 | Y | 0.79517 | 0.93262 | 0.64962 | 0.20504
0
0

## Regresson List_Office (hidden)
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions | Heating Savings Curve Comparisons
No. | Base | SGS Type | Office Size | HVAC/Fuel Type | Fuel Type | Hours | a | b | c | a | b | c |  | HDD | 1 v 10 |  | % delta
1 | Single | Single | Mid | PVAV_Elec | Electric | 2080 | 0.87047 | 0.001676 | -5.82e-08 | 2.4043 | 0.00056251 | -9.7e-09 |  | 0 | 0.87047 | 1.0451 | -20.06%
2 | Single | Single | Mid | PVAV_Elec | Electric | 2912 | 1.695 | 0.0023052 | -8.55e-08 | 3.7648 | 0.0011532 | -6.65e-08 |  | 1000 | 2.4883 | 2.7875 | -12.03%
3 | Single | Single | Mid | PVAV_Elec | Electric | 8760 | 16.0041 | 0.0025681 | -6.39e-08 | 6.1823 | 0.0040024 | -2.414e-07 |  | 2000 | 3.9896 | 4.4055 | -10.42%
4 | Single | Double | Mid | PVAV_Elec | Electric | 2080 | 1.2309 | 0.0012507 | -9.1e-09 | 4.2025 | 0.0010761 | -7.28e-08 |  | 3000 | 5.3746 | 5.8993 | -9.761%
5 | Single | Double | Mid | PVAV_Elec | Electric | 2912 | 1.9904 | 0.0018291 | -2.58e-08 | 5.4563 | 0.0024885 | -2.236e-07 |  | 4000 | 6.6432 | 7.2686 | -9.414%
6 | Single | Double | Mid | PVAV_Elec | Electric | 8760 | 19.7294 | 0.0019487 | -3.6e-08 | 7.4924 | 0.0055275 | -3.6e-07 |  | 5000 | 7.7954 | 8.5136 | -9.214%
7 | Double | Single | Mid | PVAV_Elec | Electric | 2080 | 0.36809 | 0.00078224 | -2.94e-08 | 1.2341 | 0.00086291 | -8.2844e-08 |  | 6000 | 8.8312 | 9.6343 | -9.094%
8 | Double | Single | Mid | PVAV_Elec | Electric | 2912 | 0.90209 | 0.00085224 | -1.84e-08 | 1.2423 | 0.0018367 | -1.7058e-07 |  | 7000 | 9.7506 | 10.6306 | -9.026%
9 | Double | Single | Mid | PVAV_Elec | Electric | 8760 | 10.3089 | 0.00060965 | -6.3e-09 | 1.6695 | 0.0033281 | -2.268e-07 |  | 8000 | 10.5536 | 11.5026 | -8.992%
10 | Single | Single | Large | VAV | Electric | 2080 | 1.0451 | 0.0018046 | -6.2176e-08 | 2.9952 | 0.00054436 | -1.1922e-08 |  | 9000 | 11.2401 | 12.2502 | -8.986%
11 | Single | Single | Large | VAV | Electric | 2912 | 1.9632 | 0.00248 | -8.4257e-08 | 4.691 | 0.0011371 | -6.8371e-08 |  | 10000 | 11.8103 | 12.8734 | -9.001%
12 | Single | Single | Large | VAV | Electric | 8760 | 17.8817 | 0.0027347 | -6.9507e-08 | 7.8631 | 0.0041845 | -2.5866e-07 |  | 11000 | 12.2641 | 13.3723 | -9.036%
13 | Single | Double | Large | VAV | Electric | 2080 | 1.4248 | 0.0013539 | -1.0265e-08 | 5.1829 | 0.0010799 | -8.2357e-08 |  | 12000 | 12.6015 | 13.7469 | -9.089%
14 | Single | Double | Large | VAV | Electric | 2912 | 2.3366 | 0.0019452 | -2.5309e-08 | 6.795 | 0.0025987 | -2.4798e-07
15 | Single | Double | Large | VAV | Electric | 8760 | 22.0222 | 0.0020809 | -4.0988e-08 | 9.5019 | 0.0059375 | -4.1904e-07 |  | HDD | 2 v 11 |  | % delta
16 | Double | Single | Large | VAV | Electric | 2080 | 0.4342 | 0.00085233 | -3.2055e-08 | 1.5494 | 0.00091568 | -9.2914e-08 |  | 0 | 1.695 | 1.9632 | -15.83%
17 | Double | Single | Large | VAV | Electric | 2912 | 1.0306 | 0.00093112 | -2.0723e-08 | 1.5594 | 0.0020586 | -2.0486e-07 |  | 1000 | 3.9147 | 4.3589 | -11.35%
18 | Double | Single | Large | VAV | Electric | 8760 | 11.4976 | 0.00062221 | -5.8971e-09 | 2.2115 | 0.0036711 | -2.6307e-07 |  | 2000 | 5.9633 | 6.5862 | -10.44%
19 | Single | Single | Mid | PVAV_Gas | Natural Gas | 2080 | 0.042695 | 8.1867e-05 | -2.8552e-09 | 2.4043 | 0.00056251 | -9.7e-09 |  | 3000 | 7.841 | 8.6449 | -10.25%
20 | Single | Single | Mid | PVAV_Gas | Natural Gas | 2912 | 0.083713 | 0.00011194 | -4.1327e-09 | 3.7648 | 0.0011532 | -6.65e-08 |  | 4000 | 9.5477 | 10.5351 | -10.34%
21 | Single | Single | Mid | PVAV_Gas | Natural Gas | 8760 | 0.78714 | 0.00012298 | -1.782e-07 | 6.1823 | 0.0040024 | -2.414e-07 |  | 5000 | 11.0834 | 12.2567 | -10.59%
22 | Single | Double | Mid | PVAV_Gas | Natural Gas | 2080 | 0.058867 | 6.1357e-05 | -4.908e-10 | 4.2025 | 0.0010761 | -7.28e-08 |  | 6000 | 12.448 | 13.8099 | -10.94%
23 | Single | Double | Mid | PVAV_Gas | Natural Gas | 2912 | 0.096359 | 8.942e-05 | -1.2781e-09 | 5.4563 | 0.0024885 | -2.236e-07 |  | 7000 | 13.6417 | 15.1946 | -11.38%
24 | Single | Double | Mid | PVAV_Gas | Natural Gas | 8760 | 0.95972 | 9.5436e-05 | -1.8077e-09 | 7.4924 | 0.0055275 | -3.6e-07 |  | 8000 | 14.6644 | 16.4107 | -11.91%
25 | Double | Single | Mid | PVAV_Gas | Natural Gas | 2080 | 0.017465 | 3.824e-05 | -1.454e-09 | 1.2341 | 0.00086291 | -8.2844e-08 |  | 9000 | 15.5161 | 17.4583 | -12.52%
26 | Double | Single | Mid | PVAV_Gas | Natural Gas | 2912 | 0.043295 | 4.1592e-05 | -9.041e-10 | 1.2423 | 0.0018367 | -1.7058e-07 |  | 10000 | 16.1967 | 18.3374 | -13.22%
27 | Double | Single | Mid | PVAV_Gas | Natural Gas | 8760 | 0.50115 | 2.9516e-05 | -2.97e-10 | 1.6695 | 0.0033281 | -2.268e-07 |  | 11000 | 16.7064 | 19.048 | -14.02%
28 | Single | Single | Large | VAV | Natural Gas | 2080 | 0.051034 | 8.7885e-05 | -3.0213e-09 | 2.9952 | 0.00054436 | -1.1922e-08 |  | 12000 | 17.0451 | 19.5901 | -14.93%
29 | Single | Single | Large | VAV | Natural Gas | 2912 | 0.09622 | 0.00012082 | -4.1033e-09 | 4.691 | 0.0011371 | -6.8371e-08
30 | Single | Single | Large | VAV | Natural Gas | 8760 | 0.87218 | 0.00013319 | -3.3867e-09 | 7.8631 | 0.0041845 | -2.5866e-07 |  | HDD | 3 v 12 |  | % delta
31 | Single | Double | Large | VAV | Natural Gas | 2080 | 0.068584 | 6.5753e-05 | -4.825e-10 | 5.1829 | 0.0010799 | -8.2357e-08 |  | 0 | 16.0041 | 17.8817 | -11.73%
32 | Single | Double | Large | VAV | Natural Gas | 2912 | 0.11084 | 9.4884e-05 | -1.2252e-09 | 6.795 | 0.0025987 | -2.4798e-07 |  | 1000 | 18.5083 | 20.5469 | -11.01%
33 | Single | Double | Large | VAV | Natural Gas | 8760 | 1.0746 | 0.00010117 | -2.0052e-09 | 9.5019 | 0.0059375 | -4.1904e-07 |  | 2000 | 20.8848 | 23.0731 | -10.48%
34 | Double | Single | Large | VAV | Natural Gas | 2080 | 0.021081 | 4.1282e-05 | -1.5477e-09 | 1.5494 | 0.00091568 | -9.2914e-08 |  | 3000 | 23.1334 | 25.4603 | -10.06%
35 | Double | Single | Large | VAV | Natural Gas | 2912 | 0.049487 | 4.5563e-05 | -1.0305e-09 | 1.5594 | 0.0020586 | -2.0486e-07 |  | 4000 | 25.2543 | 27.7085 | -9.718%
36 | Double | Single | Large | VAV | Natural Gas | 8760 | 0.5567 | 3.1069e-05 | -3.498e-10 | 2.2115 | 0.0036711 | -2.6307e-07 |  | 5000 | 27.2473 | 29.8176 | -9.433%
[14 empty] | 6000 | 29.1125 | 31.7878 | -9.189%
Peak Load Reduction Regressions | [6 empty] | Regression Form (a+bx+cx^2) | [6 empty] | 7000 | 30.85 | 33.6189 | -8.975%
[7 empty] | Baseline Cooling Load Coefficients |  |  | Cooling Coefficients |  |  |  | 8000 | 32.4596 | 35.311 | -8.784%
No. | Base | SGS Type | Office Size | HVAC System Type | Location |  | a | b | c | a | b | c |  | 9000 | 33.9415 | 36.8641 | -8.611%
1 | Single | Single | Mid |  |  |  | 19.7937 | 0.0034283 | -3.153e-07 | 21.1474 | 0.0060445 | -5.603e-07 |  | 10000 | 35.2955 | 38.2782 | -8.451%
2 | Single | Double | Mid |  |  |  | 19.7937 | 0.0034283 | -3.153e-07 | 45.4062 | 0.0096502 | -8.115e-07 |  | 11000 | 36.5218 | 39.5533 | -8.301%
3 | Double | Single | Mid |  |  |  | 17.8041 | 0.0027898 | -2.34e-07 | 15.6944 | 0.0034111 | -2.989e-07 |  | 12000 | 37.6202 | 40.6894 | -8.158%
4 | Single | Single | Large |  |  |  | 24.3073 | 0.0023954 | -2.005e-07 | 19.9673 | 0.0070543 | -7.612e-07
5 | Single | Double | Large |  |  |  | 24.3073 | 0.0023954 | -2.005e-07 | 46.0266 | 0.011787 | -1.1328e-06
6 | Double | Single | Large |  |  |  | 23.0197 | 0.0015842 | -7.35e-08 | 16.6364 | 0.0047085 | -5.485e-07
Baseline EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type | Office Size | Fuel | Location | Hours | a | b | c
1 | Single | N/A | Mid | Electric | N/A | 2080 | 55.1811 | -0.002839 | 4.1e-07
2 | Single | N/A | Mid | Electric | N/A | 2912 | 69.3419 | -0.0051025 | 6.6e-07
3 | Single | N/A | Mid | Electric | N/A | 8760 | 155.2883 | -0.012402 | 1.42e-06
4 | Double | N/A | Mid | Electric | N/A | 2080 | 56.4687 | -0.0036288 | 3.8e-07
5 | Double | N/A | Mid | Electric | N/A | 2912 | 66.1222 | -0.0050973 | 6e-07
6 | Double | N/A | Mid | Electric | N/A | 8760 | 132.8104 | -0.007426 | 8.1e-07
7 | Single | N/A | Mid | Gas | N/A | 2080 | 59.3124 | -0.00244 | 4.1e-07
8 | Single | N/A | Mid | Gas | N/A | 2912 | 74.8824 | -0.0048032 | 1.115e-06
9 | Single | N/A | Mid | Gas | N/A | 8760 | 163.5203 | -0.0062067 | 9.8e-07
10 | Double | N/A | Mid | Gas | N/A | 2080 | 59.7013 | -0.0047265 | 4.7e-07
11 | Double | N/A | Mid | Gas | N/A | 2912 | 70.9425 | -0.0063586 | 6.5e-07
12 | Double | N/A | Mid | Gas | N/A | 8760 | 139.89 | -0.010483 | 1.14e-06
13 | Single | N/A | Large | Electric | N/A | 2080 | 58.2415 | -0.00473 | 7.1e-07
14 | Single | N/A | Large | Electric | N/A | 2912 | 90.2995 | -0.0075784 | 1.08e-06
15 | Single | N/A | Large | Electric | N/A | 8760 | 151.3971 | -0.0088017 | 1.21e-06
16 | Double | N/A | Large | Electric | N/A | 2080 | 59.5296 | 0.0058856 | 7.8e-07
17 | Double | N/A | Large | Electric | N/A | 2912 | 88.8428 | -0.0088189 | 1.16e-06
18 | Double | N/A | Large | Electric | N/A | 8760 | 143.1419 | -0.0096109 | 1.16e-06
19 | Single | N/A | Large | Gas | N/A | 2080 | 59.4612 | -0.0041882 | 6e-07
20 | Single | N/A | Large | Gas | N/A | 2912 | 93.5545 | -0.0066678 | 1.02e-06
21 | Single | N/A | Large | Gas | N/A | 8760 | 154.7148 | -0.0065439 | 1.04e-06
22 | Double | N/A | Large | Gas | N/A | 2080 | 61.096 | -0.0049 | 6.7e-07
23 | Double | N/A | Large | Gas | N/A | 2912 | 90.4449 | -0.0066078 | 9.2e-07
24 | Double | N/A | Large | Gas | N/A | 8760 | 151.3476 | -0.010117 | 1.22e-06
Cooling Adjustment Regressoins Regressions | [6 empty] | a | b | c | d
Mid-size Office | [6 empty] | 0.69722 | -0.00010782 | 3.6051e-08 | -6.4e-12
Large Office | [6 empty] | 0.7793 | 4.963e-05 | -2.8839e-08 | 1e-12

## Regresson List_SH (hidden)
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Heating Coefficients (Part 2)
No. | Base | CSW Type | Hotel Size | HVAC/Fuel Type | Fuel Type | Occupancy | a | b | c | a | b | c
1 | Single | Single | Small | PTAC | Electric | 33 | 0.26195 | 0.0011672 | 7.07e-08 | 1.0416 | 0.0014359 | -7.425e-08
2 | Single | Single | Small | PTAC | Electric | 100 | 0.34628 | 0.0017406 | 3.3033e-08 | 1.9828 | 0.0013242 | -3.5574e-08
3 | Single | Double | Small | PTAC | Electric | 33 | 0.33832 | 0.00093325 | 8.5301e-08 | 2.4891 | 0.0025642 | -1.423e-07
4 | Single | Double | Small | PTAC | Electric | 100 | 0.45927 | 0.0014362 | 5.3247e-08 | 3.861 | 0.0026635 | -1.156e-07
5 | Double | Single | Small | PTAC | Electric | 33 | 0.23855 | 0.00024276 | 5.61e-08 | 0.77436 | 0.0011276 | -6.5352e-08
6 | Double | Single | Small | PTAC | Electric | 100 | 0.23945 | 0.00080163 | 1.4955e-08 | 0.96197 | 0.0013188 | -6.1448e-08
7 | Single | Single | Small | PTHP | Electric | 33 | 0.11905 | 0.00042364 | 4.7421e-08 | 1.0416 | 0.0014359 | -7.425e-08 | 47.5036 | -0.011031 | 7.4216e-07
8 | Single | Single | Small | PTHP | Electric | 100 | 0.14734 | 0.00065798 | 3.4171e-08 | 1.9828 | 0.0013242 | -3.5574e-08 | 47.5333 | -0.010875 | 7.3864e-07
9 | Single | Double | Small | PTHP | Electric | 33 | 0.15066 | 0.00032914 | 5.2461e-08 | 2.4891 | 0.0025642 | -1.423e-07 | 47.4252 | -0.011071 | 7.4204e-07
10 | Single | Double | Small | PTHP | Electric | 100 | 0.19401 | 0.0005347 | 4.1346e-08 | 3.861 | 0.0026635 | -1.156e-07 | 47.8443 | -0.011024 | 7.4493e-07
11 | Double | Single | Small | PTHP | Electric | 33 | 0.10405 | 7.4317e-05 | 3.079e-08 | 0.77436 | 0.0011276 | -6.5352e-08 | 23.4641 | -0.0055318 | 3.6817e-07
12 | Double | Single | Small | PTHP | Electric | 100 | 0.099065 | 0.00030373 | 1.5623e-08 | 0.96197 | 0.0013188 | -6.1448e-08 | 21.9388 | -0.0050138 | 3.4055e-07
Peak Load Reduction Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Base Peak Load Coefficient |  |  | Cooling Reduction Coefficients
No. | Base | SGS Type | Hotel Size | HVAC System Type | Location |  | a | b | c | a | b | c
1 | Single | Single | Small | N/A | N/A |  | 16.4825 | 0.0040935 | -3.244e-07 | 13.683 | 0.0061771 | -5.891e-07
2 | Single | Double | Small | N/A | N/A |  | 16.4825 | 0.0040935 | -3.244e-07 | 24.7902 | 0.011711 | -1.1299e-06
3 | Double | Single | Small | N/A | N/A |  | 16.2543 | 0.0040813 | -4.02e-07 | 8.6455 | 0.0043684 | -4.061e-07
EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type | Hotel Size | HVAC/Fuel Type | Location | Occupancy | a | b | c
1 | Single | N/A | Small | PTAC | N/A | 33 | 53.3842 | -0.0018385 | 5.912e-07
3 | Single | N/A | Small | PTAC | N/A | 100 | 61.7548 | -0.0028943 | 6.6e-07
4 | Double | N/A | Small | PTAC | N/A | 33 | 56.6258 | -0.0021877 | 5.948e-07
6 | Double | N/A | Small | PTAC | N/A | 100 | 61.9924 | -0.0031041 | 6.701e-07
7 | Single | N/A | Small | PTHP | N/A | 33 | 50.7112 | -0.0053321 | 7.588e-07
9 | Single | N/A | Small | PTHP | N/A | 100 | 56.6865 | -0.0055582 | 7.785e-07
10 | Double | N/A | Small | PTHP | N/A | 33 | 48.8359 | -0.0046747 | 6.767e-07
12 | Double | N/A | Small | PTHP | N/A | 100 | 55.8014 | -0.0047838 | 6.515e-07
Cooling / Aux Split Regression |  |  | a | b | c | d
|  |  | 0.46864 | -0.00036016 | 1.0366e-07 | -1e-11

## Regresson List_LH (hidden)
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2) except PTHP which is Exponential Curve
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions
No. | Base | CSW Type | Hotel Size | HVAC/Fuel Type | Fuel Type | Occupancy | a | b | c | a | b | c
1 | Single | Single | Large |  | Electric | 33 | 0.073084 | 0.0015018 | 5.58e-08 | 1.4544 | 0.0013875 | -1.4583e-07
2 | Single | Single | Large |  | Electric | 100 | 0.12034 | 0.0024094 | 1.8e-09 | 1.5533 | 0.0013932 | -1.0309e-07
3 | Single | Double | Large |  | Electric | 33 | 0.070141 | 0.0014413 | 5.3553e-08 | 3.6119 | 0.0022594 | -1.5963e-07
4 | Single | Double | Large |  | Electric | 100 | 0.1137 | 0.0022766 | 1.7008e-09 | 5.1386 | 0.0022843 | -1.7886e-07
5 | Double | Single | Large |  | Electric | 33 | 0.06028 | 0.00045338 | 3.39e-08 | 1.1359 | 0.00073483 | -6.2573e-08
6 | Double | Single | Large |  | Electric | 100 | 0.076565 | 0.00079565 | 1.82e-08 | 1.2208 | 0.0010002 | -1.033e-07
7 | Single | Single | Large |  | Gas | 33 | 0.003117 | 6.405e-05 | 2.3799e-09 | 1.4544 | 0.0013875 | -1.4583e-07
8 | Single | Single | Large |  | Gas | 100 | 0.0051324 | 0.00010276 | 7.68e-11 | 1.5533 | 0.0013932 | -1.0309e-07
9 | Single | Double | Large |  | Gas | 33 | 0.0029915 | 6.1471e-05 | 2.284e-09 | 3.6119 | 0.0022594 | -1.5963e-07
10 | Single | Double | Large |  | Gas | 100 | 0.0048495 | 9.7096e-05 | 7.25e-11 | 5.1386 | 0.0022843 | -1.7886e-07
11 | Double | Single | Large |  | Gas | 33 | 0.002571 | 1.9337e-05 | 1.4458e-09 | 1.1359 | 0.00073483 | -6.2573e-08
12 | Double | Single | Large |  | Gas | 100 | 0.0032655 | 3.3935e-05 | 7.762e-10 | 1.2208 | 0.0010002 | -1.033e-07
Peak Load Reduction Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Base Peak Load Coefficient |  |  | Cooling Reduction Coefficients
No. | Base | SGS Type | Hotel Size | HVAC System Type | Location |  | a | b | c | a | b | c
1 | Single | Single | Large | N/A | N/A |  | 18.2091 | 0.003432 | -3.254e-07 | 4.7001 | 0.0025964 | -2.7e-07
2 | Single | Double | Large | N/A | N/A |  | 18.2091 | 0.003432 | -3.254e-07 | 7.3053 | 0.0045919 | -4.719e-07
3 | Double | Single | Large |  |  |  | 14.609 | 0.0043665 | -4.975e-07 | 3.2702 | 0.0015216 | -1.423e-07
Baseline EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type | Hotel Size | Fuel Type | Location | Occ | a | b | c
1 | Single | N/A | Large | Electric | N/A | 33 | 110.1377 | -0.0078283 | 9.88e-07
3 | Single | N/A | Large | Electric | N/A | 100 | 116.4981 | -0.0084816 | 1.0438e-06
4 | Double | N/A | Large | Electric | N/A | 33 | 103.0964 | -0.007085 | 8.928e-07
6 | Double | N/A | Large | Electric | N/A | 100 | 109.3794 | -0.0075483 | 9.197e-07
7 | Single | N/A | Large | Gas | N/A | 33 | 111.2992 | -0.0071869 | 1.0628e-06
9 | Single | N/A | Large | Gas | N/A | 100 | 117.6789 | -0.0078209 | 1.1174e-06
10 | Double | N/A | Large | Gas | N/A | 33 | 104.1237 | -0.0065781 | 9.638e-07
12 | Double | N/A | Large | Gas | N/A | 100 | 110.7392 | -0.0074406 | 1.0281e-06
Cooling / Aux Split Regression |  |  | a | b | c | d
|  |  | 0.62037 | -0.0001621 | -5.1812e-08 | -4e-12

## Regresson List_PS (hidden)
Energy Savings Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions (change from red to black when coefficients are dialed in)
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c | a | b | c
1 | Single | Single |  | FCU | Elec | 0.053961 | 0.0021448 | -1.7946e-09 | 0.95809 | 0.00022102 | -1.2262e-09
2 | Single | Double |  | FCU | Elec | 0.13779 | 0.0019761 | -5.2529e-09 | 1.3489 | 0.00071388 | -1.9599e-08
3 | Double | Single |  | FCU | Elec | 0.0037853 | 0.0010767 | 7.4261e-09 | 0.81031 | 0.00018948 | -2.1621e-09
4 | Single | Single |  | VAV | Elec | 0.28479 | 0.0029384 | -2.75e-08 | 3.6664 | 0.0013575 | -7.74e-08
5 | Single | Double |  | VAV | Elec | 0.15624 | 0.0029248 | -2.49e-08 | 5.4819 | 0.0025477 | -1.718e-07
6 | Double | Single |  | VAV | Elec | 0.60465 | 0.0020275 | -1.47e-08 | 3.0243 | 0.001035 | -4.63e-08
7 | Single | Single |  | FCU | Gas | 0.0023014 | 9.1475e-05 | -7.65e-11 | 0.95809 | 0.00022102 | -1.2262e-09
8 | Single | Double |  | FCU | Gas | 0.0058768 | 8.4279e-05 | -2.24e-10 | 1.3489 | 0.00071388 | -1.9599e-08
9 | Double | Single |  | FCU | Gas | 0.00016144 | 4.5922e-05 | 3.167e-10 | 0.81031 | 0.00018948 | -2.1621e-09
10 | Single | Single |  | VAV | Gas | 0.012146 | 0.00012532 | -1.1729e-09 | 3.6664 | 0.0013575 | -7.74e-08
11 | Single | Double |  | VAV | Gas | 0.0066635 | 0.00012474 | -1.062e-09 | 5.4819 | 0.0025477 | -1.718e-07
12 | Double | Single |  | VAV | Gas | 0.025788 | 8.6472e-05 | -6.27e-10 | 3.0243 | 0.001035 | -4.63e-08
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Base Peak Load Coefficient |  |  | Cooling Coefficients
No. | Base | HVAC Type | CSW Type | Fuel |  | a | b | c | a | b | c
1 | Single | VAV | Single | N/A |  | 23.1195 | 0.0061556 | -6.276e-07 | 21.1987 | 0.0056719 | -4.592e-07
2 | Single | VAV | Double | N/A |  | 23.0244 | 0.0060725 | -5.973e-07 | 40.881 | 0.0063162 | -4.52e-08
3 | Double | VAV | Single | N/A |  | 20.816 | 0.0054447 | -4.64e-07 | 13.1679 | 0.0036668 | -3.665e-07
4 | Single | FCU | Single | N/A |  | 23.1195 | 0.0061556 | -6.276e-07 | 21.1987 | 0.0056719 | -4.592e-07
5 | Single | FCU | Double | N/A |  | 23.0244 | 0.0060725 | -5.973e-07 | 40.881 | 0.0063162 | -4.52e-08
6 | Double | FCU | Single | N/A |  | 20.816 | 0.0054447 | -4.64e-07 | 13.1679 | 0.0036668 | -3.665e-07
Baseline EUI Regressions | [5 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c
1 | Single | N/A |  | VAV | Elec | 50.1109 | -0.0019976 | 6.983e-07
2 | Double | N/A |  | VAV | Elec | 48.2583 | -0.0023833 | 6.748e-07
3 | Single | N/A |  | VAV | Gas | 50.6134 | -0.0014571 | 7.744e-07
4 | Double | N/A |  | VAV | Gas | 48.767 | -0.0019935 | 7.509e-07
5 | Single | N/A |  | FCU | Elec | 34.7028 | 0.00039535 | 5.551e-07
6 | Double | N/A |  | FCU | Elec | 33.3119 | 0.00035673 | 4.938e-07
7 | Single | N/A |  | FCU | Gas | 36.0445 | 0.00018573 | 6.944e-07
8 | Double | N/A |  | FCU | Gas | 35.7159 | -0.00032935 | 6.558e-07

## Regresson List_SS (hidden)
Energy Savings Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions (change from red to black when coefficients are dialed in)
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c | a | b | c
1 | Single | Single |  | FCU | Elec | 0.07667 | 0.0023295 | -1.4e-09 | 1.0341 | 0.00022722 | -6e-10
2 | Single | Double |  | FCU | Elec | 0.16046 | 0.0021483 | -5.3467e-09 | 1.4756 | 0.00086338 | -2.23e-08
3 | Double | Single |  | FCU | Elec | 0.013688 | 0.001141 | 1.15e-08 | 0.87462 | 0.00019487 | -1.7e-09
4 | Single | Single |  | VAV | Elec | 0.30646 | 0.0032212 | -2.0506e-08 | 3.7648 | 0.001538 | -9.924e-08
5 | Single | Double |  | VAV | Elec | 0.26912 | 0.0030125 | -2.7017e-08 | 6.0997 | 0.0029145 | -2.0178e-07
6 | Double | Single |  | VAV | Elec | 0.60649 | 0.0021689 | -4.0728e-09 | 3.118 | 0.0011289 | -3.6959e-08
7 | Single | Single |  | FCU | Gas | 0.00327 | 9.9355e-05 | -5.97e-11 | 1.0341 | 0.00022722 | -6e-10
8 | Single | Double |  | FCU | Gas | 0.0068438 | 9.1624e-05 | -2.28e-10 | 1.4756 | 0.00086338 | -2.23e-08
9 | Double | Single |  | FCU | Gas | 0.0005838 | 4.8664e-05 | 4.905e-10 | 0.87462 | 0.00019487 | -1.7e-09
10 | Single | Single |  | VAV | Gas | 0.013071 | 0.00013738 | -8.746e-10 | 3.7648 | 0.001538 | -9.924e-08
11 | Single | Double |  | VAV | Gas | 0.011478 | 0.00012849 | -1.1523e-09 | 6.0997 | 0.0029145 | -2.0178e-07
12 | Double | Single |  | VAV | Gas | 0.030167 | 9.1132e-05 | -8.22e-11 | 3.118 | 0.0011289 | -3.6959e-08
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Base Peak Load Coefficient |  |  | Cooling Coefficients
No. | Base | HVAC Type | CSW Type | Fuel |  | a | b | c | a | b | c
1 | Single | VAV | Single | N/A |  | 14.0663 | 0.0051478 | -5.317e-07 | 18.6274 | 0.0062097 | -6.352e-07
2 | Single | VAV | Double | N/A |  | 13.259 | 0.0058206 | -6.029e-07 | 37.7857 | 0.0078383 | -6.158e-07
3 | Double | VAV | Single | N/A |  | 12.3843 | 0.0049067 | -4.9e-07 | 12.5508 | 0.0030735 | -2.484e-07
4 | Single | FCU | Single | N/A |  | 14.0663 | 0.0051478 | -5.317e-07 | 18.6274 | 0.0062097 | -6.352e-07
5 | Single | FCU | Double | N/A |  | 13.259 | 0.0058206 | -6.029e-07 | 37.7857 | 0.0078383 | -6.158e-07
6 | Double | FCU | Single | N/A |  | 12.3843 | 0.0049067 | -4.9e-07 | 12.5508 | 0.0030735 | -2.484e-07
Baseline EUI Regressions | [5 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c
1 | Single | N/A |  | VAV | Elec | 53.562 | -0.0013443 | 1.1176e-06
2 | Double | N/A |  | VAV | Elec | 52.0153 | -0.0017659 | 1.0907e-06
3 | Single | N/A |  | VAV | Gas | 53.9476 | -0.00045128 | 1.2431e-06
4 | Double | N/A |  | VAV | Gas | 52.3491 | -0.00076439 | 1.1884e-06
5 | Single | N/A |  | FCU | Elec | 46.581 | -0.0009915 | 1.1638e-06
6 | Double | N/A |  | FCU | Elec | 45.9373 | -0.0016372 | 1.1558e-06
7 | Single | N/A |  | FCU | Gas | 47.0639 | -0.00053891 | 1.3252e-06
8 | Double | N/A |  | FCU | Gas | 46.471 | -0.0013285 | 1.3182e-06
Cooling / Aux Split Regression |  |  | a | b | c | d
| VAV |  | 0.54363 | -0.0002672 | 6.9504e-08 | -7e-12
| FCU |  | 0.94835 | -0.00023927 | 5.443e-09 | 1e-12

## Regresson List_Hosp (hidden)
Energy Savings Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c | a | b | c
1 | Single | Single |  | VAV | Elec | 19.2535 | 0.0021028 | -2.52e-08 | 8.3588 | 0.0051741 | -4.5098e-07 |  | -0.27284 | 0.0039845 | -2.1953e-07 | 1.5741 | 0.0081792 | -4.4986e-06
2 | Single | Double |  | VAV | Elec | 26.1154 | 0.0017024 | -1.44e-08 | 10.0933 | 0.0072545 | -6.7343e-07 |  | 0.074575 | 0.003999 | -2.8628e-07 | 0.78588 | 0.0092962 | -5.2852e-06
3 | Double | Single |  | VAV | Elec | 13.5118 | 0.00071769 | 2.8786e-09 | 3.6366 | 0.0042105 | -3.3164e-07 |  | 2.4796 | 0.0030728 | -1.6648e-07 | 1.6499 | 0.012552 | -6.349e-06
4 | Single | Single |  | VAV | Gas | 0.80257 | 9.1983e-05 | -1.2e-09 | 8.3588 | 0.0051741 | -4.5098e-07 |  | 2.2479 | 0.0021615 | -1.5232e-07 | 0.45658 | 0.017916 | -1.0135e-05
5 | Single | Double |  | VAV | Gas | 1.1203 | 7.3165e-05 | -3e-10 | 10.0933 | 0.0072545 | -6.7343e-07 |  | 0.02227 | 0.00015822 | -8.428e-09 | 1.2666 | 0.0088125 | -4.7465e-06
6 | Double | Single |  | VAV | Gas | 0.57628 | 3.0609e-05 | -1.228e-10 | 3.6366 | 0.0042105 | -3.3164e-07 |  | -1.0558 | 0.00047562 | -3.4052e-08 | 0.78682 | 0.0092579 | -5.1559e-06
[13 empty] | -0.19323 | 0.00021308 | -1.1548e-08 | 0.8344 | 0.016489 | -8.9439e-06
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2) | [6 empty] | -0.093324 | 0.00015414 | -1.1003e-08 | 0.45982 | 0.017847 | -9.932e-06
[6 empty] | Base Peak Load Coefficient |  |  | Cooling Coefficients
No. | Base | HVAC Type | CSW Type | Fuel |  | a | b | c | a | b | c
1 | Single | VAV | Single | N/A |  | 15.9452 | 0.0062549 | -4.666e-07 | 10.2212 | 0.004944 | -4.35e-07
2 | Single | VAV | Double | N/A |  | 15.9452 | 0.0062549 | -4.666e-07 | 16.1958 | 0.010505 | -1.0237e-06
3 | Double | VAV | Single | N/A |  | 19.62 | 0.003158 | -2.394e-07 | 5.1435 | 0.003977 | -3.869e-07
Baseline EUI Regressions | [5 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c
1 | Single | N/A |  | VAV | Elec | 222.3254 | -0.008719 | 1.229e-06
2 | Double | N/A |  | VAV | Elec | 217.221 | -0.0080141 | 1.1096e-06
3 | Single | N/A |  | VAV | Gas | 238.563 | -0.0081294 | 1.3234e-06
4 | Double | N/A |  | VAV | Gas | 229.9586 | -0.0063651 | 1.1099e-06
Cooling / Aux Split Regression |  |  | a | b | c | d
|  |  | 0.71341 | -0.00019542 | 3.9398e-08 | -3e-12

## Regresson List_MF (hidden)
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions
No. | Base | SGS Type | MF Type | HVAC/Fuel Type | Location | Occ | a | b | c | a | b | c
1 | Single | Single | Low | PTAC_Elec |  |  | 0.299 | 0.0025234 | 2.3682e-08 | 2.5605 | 0.0019479 | -6e-08
2 | Single | Double | Low | PTAC_Elec |  |  | 0.28229 | 0.0015466 | 9.7967e-08 | 4.7841 | 0.0037555 | -1.745e-07
3 | Double | Single | Low | PTAC_Elec |  |  | 0.10639 | 0.0011628 | 7.3912e-09 | 1.2302 | 0.0018858 | -8.9e-08
4 | Single | Single | Mid | FCU_Elec |  |  | 0.16121 | 0.0021418 | 4.2685e-08 | 2.4323 | 0.001554 | -5.8284e-08
5 | Single | Double | Mid | FCU_Elec |  |  | 0.14207 | 0.0012868 | 1.0679e-07 | 4.5673 | 0.0034876 | -2.2003e-07
6 | Double | Single | Mid | FCU_Elec |  |  | 0.058778 | 0.00076818 | 3.9601e-08 | 1.1837 | 0.0015549 | -8.4302e-08
7 | Single | Single | Mid | FCU_Gas |  |  | 0.0068754 | 9.1347e-05 | 1.8205e-09 | 2.4323 | 0.001554 | -5.8284e-08
8 | Single | Double | Mid | FCU_Gas |  |  | 0.0060592 | 5.4883e-05 | 4.5544e-09 | 4.5673 | 0.0034876 | -2.2003e-07
9 | Double | Single | Mid | FCU_Gas |  |  | 0.0025069 | 3.2763e-05 | 1.689e-09 | 1.1837 | 0.0015549 | -8.4302e-08
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Baseline Cooling Load Coefficients |  |  | Cooling Coefficients
No. | Base | MF Type | SGS Type | Fuel |  | a | b | c | a | b | c
1 | Single | Low | Single | N/A |  | 17.8686 | 0.0046066 | -4.089e-07 | 18.7698 | 0.0049779 | -4.876e-07
2 | Single | Low | Double | N/A |  | 17.8686 | 0.0046066 | -4.089e-07 | 40.0125 | 0.0048721 | -3.419e-07
3 | Double | Low | Single | N/A |  | 15.0506 | 0.0036862 | -3.426e-07 | 14.6237 | 0.0017273 | -2.32e-08
4 | Single | Mid | Single | N/A |  | 10.3001 | 0.0027499 | -1.929e-07 | 16.6972 | 0.0055256 | -4.957e-07
5 | Single | Mid | Double | N/A |  | 10.3001 | 0.0027499 | -1.929e-07 | 34.8294 | 0.0084273 | -6.738e-07
6 | Double | Mid | Single | N/A |  | 8.7783 | 0.0021889 | -1.501e-07 | 11.1553 | 0 | -2.531e-07
Baseline EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients
No. | Base | SGS Type | MF Type | HVAC Type | Fuel |  | a | b | c | a | b | c
1 | Single | N/A | Low | PTAC | Elec |  | 53.138 | -0.0029766 | 6.102e-07 | 53.138 | -0.0029766 | 6.102e-07
2 | Double | N/A | Low | PTAC | Elec |  | 44.2378 | -0.0016118 | 4.553e-07 | 44.2378 | -0.0016118 | 4.553e-07
3 | Single | N/A | Mid | FCU | Elec |  | 47.6672 | -0.0038797 | 6.607e-07 | 47.6672 | -0.0038797 | 6.607e-07
4 | Double | N/A | Mid | FCU | Elec |  | 44.8676 | -0.0035527 | 5.671e-07 | 44.8676 | -0.0035527 | 5.671e-07
5 | Single | N/A | Mid | FCU | Gas |  | 47.7768 | -0.0034438 | 7.203e-07 | 47.7768 | -0.0034438 | 7.203e-07
6 | Double | N/A | Mid | FCU | Gas |  | 44.9531 | -0.0032699 | 6.227e-07 | 44.9531 | -0.0032699 | 6.227e-07
Savings Adjustment Factor Regressions
No. | Base | CSW Type | Single | HVAC | Fuel |  | a | b | c | d
1 | Single | Single | Low | PTAC | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
2 | Single | Double | Low | PTAC | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
3 | Double | Single | Low | PTAC | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
4 | Single | Single | Mid | FCU | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
5 | Single | Double | Mid | FCU | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
6 | Double | Single | Mid | FCU | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
7 | Single | Single | Mid | FCU | Gas |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
8 | Single | Double | Mid | FCU | Gas |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
9 | Double | Single | Mid | FCU | Gas |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
Savings Adjustment Factor Regressions (Cool)
No. | Base | CSW Type | MF Type | HVAC | Fuel |  | a | b | c | d
1 | Single | Single | Low | PTAC | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
2 | Single | Double | Low | PTAC | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
3 | Double | Single | Low | PTAC | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
4 | Single | Single | Mid | FCU | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
5 | Single | Double | Mid | FCU | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
6 | Double | Single | Mid | FCU | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
7 | Single | Single | Mid | FCU | Gas |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
8 | Single | Double | Mid | FCU | Gas |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
9 | Double | Single | Mid | FCU | Gas |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
Cooling Adjustment Regressoins Regressions | [6 empty] | a | b | c | d
Mid-size | [6 empty] | 0.86172 | -0.00029049 | 7.5e-08 | -1e-11
Low-rise | [6 empty] | 0.64499 | -0.00035283 | 9.583e-08 | -1e-11

## Lists (hidden)
Type of Glass | State | Alabama | Alaska | Arizona | Arkansas | California | Colorado | Connecticut | Delaware | Florida | Georgia | Hawaii | Idaho | Illinois | Indiana | Iowa | Kansas | Kentucky | Louisiana | Maine | Maryland | Massachusetts | Michigan | Minnesota | Mississippi | Missouri | Montana | Nebraska | Nevada | New_Hampshire | New_Jersey | New_Mexico | New_York | North_Carolina | North_Dakota | Ohio | Oklahoma | Oregon | Pennsylvania | Rhode_Island | South_Carolina | South_Dakota | Tennessee | Texas | Utah | Vermont | Virginia | Washington | West_Virginia | Wisconsin | Wyoming | Dist._of_Columbia | SGS Type | Fuel | HVAC Type, Office | Building Type | Occ | Infil | Cooling
Single pane | Alabama | Anniston | Adak | Casa Granda | Batesville | Alturas | Akron CO | Danbury | Dover | Crestview | Albany GA | Hilo | Boise | Aurora IL | Bloomington IN | Algona | Chanute | Bowling Green | Alexandria LA | Auburn ME | Baltimore | Beverly | Alpena | Aitkin | Biloxi | Cape Girardeau | Billings | Ainsworth | Elko | Berlin | Atlantic City | Alamogordo | Albany NY | Asheville | Bismarck | Akron OH | Altus | Astoria | Allentown | New Shoreham | Anderson | Aberdeen SD | Blountville | Abilene | Blanding | Burlington VT | Abingdon | Aberdeen WA | Beckley | Antigo | Casper | Washington DC | Single | Electric | Packaged VAV with electric reheat | Office | 33% | Included | Yes
Double pane | Alaska | Auburn AL | Anchorage | Douglas | Bentonville | Bakersfield | Alamosa | Groton | Wilmington DE | Daytona | Alma | Honolulu | Burley | Belleville | Evansville | Atlantic | Concordia | Fort Knox | Baton Rouge | Augusta ME | Camp Springs | Boston | Ann Arbor | Albert Lea | Columbus MS | Columbia MO | Bozeman | Alliance | Ely | Concord NH | Belmar | Albuquerque | Binghamton | Cape Hatteras | Devils Lake | Cincinnati | Bartlesville | Aurora OR | Altoona | Pawtucket | Beaufort | Brookings | Chattanooga | Alice | Bryce Canyon City | Montpelier | Blacksburg | Bellingham | Bluefield | Appleton | Cheyenne |  | Double | Natural Gas | Packaged VAV with hydronic reheat | Hotel | 66% | Excluded | No
New double pane (U<0.35) | Arizona | Birmingham | Aniak | Flagstaff | El Dorado | Bishop | Aspen | Hartford Brainard |  | Fort Lauderdale | Athens | Kahului | Caldwell | Bloomington IL | Fort Wayne | Boone | Dodge City | Hebron | Bossier City | Bangor | Hagerstown | Chicopee Falls | Battle Creek | Alexandria MN | Greenville MS | Farmington MO | Butte | Beatrice | Fallon | Keene | Fairfield NJ | Carlsbad NM | Buffalo | Charlotte | Dickinson | Cleveland | Clinton OK | Baker City | Bradford | Providence | Charleston SC | Huron | Crossville | Amarillo | Cedar City | Rutland | Charlottesville | Bremerton | Bridgeport | Eau Claire | Cody |  |  | None | Built-up VAV with hydronic reheat | Primary School | 100%
| Arkansas | Daleville | Annette Island | Grand Canyon | Fayetteville AR | Blue Canyon | Aurora CO | New Haven |  | Fort Myers | Atlanta | Kalaoa | Coeur d'Alene | Bondville | Huntingburg | Burlington IA | Emporia | Henderson City | Houma | Bar Harbor | Lexington Park | Hyannis | Benton Harbor | Austin MN | Greenwood | Ft. Leonard Wood | Cut Bank | Bellevue | Las Vegas NV | Laconia | Millville | Clayton | Elmira | Elizabeth City | Fargo | Columbus OH | Enid | Burns | Butler |  | Columbia SC | Mitchell | Dyersburg | Austin TX | Delta | Springfield VT | Danville | Ephrata | Charleston WV | Green Bay | Evanston |  |  |  | Other | Secondary School
| California | Dothan | Anvik | Kingman | Flippin | Blythe | Broomfield | Oxford |  | Fort Pierce | Augusta GA | Kaneohe | Grand View | Chicago | Indianapolis | Carroll | Garden City | Hopkinsville | Lafayette LA | Brunswick ME | Salisbury | Lawrence | Cadillac | Baudette | Gulfport | Jefferson City | Glasgow | Broken Bow | Lovelock | Lebanon | Newark | Clovis | Glen Falls | Fayetteville NC | Grand Forks | Dayton | Fort Sill | Corvallus | DuBois |  | Florence | Mobridge | Jackson TN | Brownsville | Hanksville |  | Farmville | Everett | Elkins | Janesville | Gillette |  |  | Electric Only |  | Hospital
| Colorado | Gadsen | Big River Lakes | Luke | Fort Smith | Burbank | Colorado Springs | Stratford |  | Gainesville | Brunswick GA | Kapalua | Hailey | Decatur | Kokomo | Cedar Rapids | Goodland | Jackson KY | Lake Charles | Caribou |  | Marthas Vineyard | Calumet | Bemidji | Hattiesburg | Joplin | Glendive | Chadron | Mercury | Manchester | Rio Grande | Deming | Jamestown NY | Goldsboro | Jamestown ND | Findlay | Gage | Eugene | Erie |  | Greenville SC | Pierre | Knoxville TN | Childress | Moab |  | Franklin VA | Forks | Huntington | La Cross | Jackson Hole |  |  | Electric | HVAC Type, Hotel | Multi-family
| Connecticut | Huntsville | Birchwood | Page | Harrison | Camarillo | Cortez |  |  | Homestead | Columbus GA | Kapolei | Idaho Falls | Marion IL | Lafayette IN | Chariton | Great Bend | Lexington | Leesville | Frenchville |  | Mashpee | Detroit | Benson | Jackson MS | Kaiser | Great Falls | Columbus NE | Reno | Mount Washington | Teterboro | Farmington NM | Massena | Greensboro | Minot | Mansfield | Hobart | Klamath Falls | Franklin PA |  | Greer | Rapid City | Memphis | College Station | Ogden |  | Fredericksburg | Hanford | Lewisburg | Lone Rock | Lander |  |  | None | PTAC | Other
| Delaware | Mobile | Chulitna | Phoenix | Hot Springs AR | Camp Pendleton | Craig |  |  | Jacksonville FL | Macon | Kapolei | Lewiston | Moline | Muncie | Charles City | Hays | London | Monroe | Houlton |  | Nantucket | Escanaba | Brainerd | McComb | Kansas City | Havre | Falls City | Tonopah | Portsmouth | Trenton | Gallup | Monticello NY | Greenville NC | Williston | Toledo OH | Lawton | La Grande | Harrisburg |  | Myrtle Beach | Sioux Falls | Nashville | Corpus Christi | Provo |  | Hampton | Hoquiam | Martinsburg | Madison | Laramie |  |  |  | PTHP
| Dist._of_Columbia | Montgomery | Cold Bay | Prescott | Jonesboro | Carlsbad CA | Denver |  |  | Key West | Marietta | Lanai | Malad City | Mount Vernon | South Bend | Clarinda | Hill City | Louisville | New Iberia | Millinocket |  | New Bedford | Flint | Cambridge | Meridian | Kirksville | Helena | Fremont | Winnemucca |  |  | Las Cruces | New Windsor | Havelock |  | Youngstown | McAlester | Lakeview | Johnstown |  | North Myrtle Beach | Watertown SD |  | Cotulla | Saint George |  | Hillsville | Kelso | Morgantown | Manitowac | Rawlins |  |  |  | Fan Coil Unit
| Florida | Muscle Shoals | Cordova | Safford | Little Rock | Chino | Durango |  |  | Lakeland | Rome | Lihue | Pocatello | Murphysboro | Terre Haute | Clinton IA | Hutchinson KS | Somerset | New Orleans | Portland ME |  | North Adams | Freeland | Cloquet | Natchez | Poplar Bluff | Kalispell | Grand Island |  |  |  | Las Vegas NM | New York | Hickory |  | Zanesville | Oklahoma City | Medford | Lancaster PA |  | Sumter | Yankton |  | Dalhart | Salt Lake City |  | Hot Springs VA | Moses Lake | parkersburg | Marshfield | Riverton |  |  |  | Other
| Georgia | Troy | Dillingham | Scottsdale | Pine Bluff | Chula Vista | Fort Collins |  |  | Marathon | Savannah | Molokai | Salmon | Peoria |  | Council Bluffs | Junction City | West Paducah | Patterson | Presque Isle |  | Norwood | Grand Rapids MI | Crane Lake | Starkville | Springfield MO | Lewistown | Hastings |  |  |  | Roswell | Nigara Falls | Jacksonville NC |  |  | Ponca City | North Bend | Middletown |  |  |  |  | Dallas | Vernal |  | Leesburg | Olympia | Wheeling | Milwaukee | Rock Springs
| Hawaii | Tuscaloosa | Dutch Harbor | Show Low | Rogers | Concord CA | Grand Junction |  |  | Mayport | Valdosta |  | Soda Springs | Quincy |  | Creston | Liberal |  | Pineville | Rockland |  | Plymouth | Houghton Lake | Crookston | Tupelo | St. Joseph | Livingston | Holdrege |  |  |  | Ruidoso | Republic | Kinston |  |  | Stillwater | Pendleton | Philadelphia |  |  |  |  | Del Rio | Wendover |  | Lynchburg | Pasco |  | Minocqua | Sheridan |  |  |  | HVAC Type, School
| Idaho |  | Emmonak | Tucson | Siloam Spring | Crescent City | Greeley |  |  | Melbourne | Warner Robins |  | Twin Falls | Rock Falls |  | Decorah | Manhattan |  | Shreveport | Sanford |  | Provincetown | Howell | Detroit Lakes |  | St. Louis | Miles City | Imperial NE |  |  |  | Santa Fe | Rockester | Manteo |  |  | Tulsa | Portland OR | Pittsburgh |  |  |  |  | El Paso |  |  | Manassas | Port Angeles |  | Mosinee | Workland |  |  |  | Central Ducted VAV
| Illinois |  | Fairbanks | Winslow | Springdale | Daggett | Gunnison |  |  | Miami |  |  |  | Rockford |  | Denison | Newton KS |  |  | Waterville |  | Westfield | Ironwood | Duluth |  | Vichy | Missoula | Kearney |  |  |  | Taos | Ronkonkoma | New Bern |  |  |  | Redmond | Reading |  |  |  |  | Galveston |  |  | Marion VA | Pullman |  | Oshkosh |  |  |  |  | Fan Coil Unit
| Indiana |  | Gustavus | Yuma | Stuttgart | Fairfield CA | Gypsum |  |  | Milton |  |  |  | Springfield IL |  | Des Moines | Olathe |  |  | Wiscasset |  | Worchester | Jackson MI | Ely |  | Warrensburg | Sidney MT | Lincoln |  |  |  | Truth or Consequences | Saranac Lake | Raleigh |  |  |  | Roseburg | Scranton |  |  |  |  | Georgetown |  |  | Martinsville | Renton |  | Phillips |  |  |  |  | Other
| Iowa |  | Healy |  | Texarkana | Fresno | Hayden |  |  | Naples |  |  |  | West Chicago |  | Dubuque | Russell | [5 empty] | Kalamazoo | Eveleth |  |  | Wolf Point | McCook |  |  |  | Tucumcari | Syracuse | Rocky Mount |  |  |  | Salem | University Park |  |  |  |  | Greenville TX |  |  | Melfa | Seattle |  | Rhinelander
| Kansas |  | Homer |  | Walnut Ridge | Fullerton | La Junta |  |  | Ocala | [5 empty] | Estherville | Salina | [5 empty] | Kincheloe | Fairmont |  |  |  | Norfolk NE |  |  |  |  | Utica | Southern Pines |  |  |  | Sexton Summit | Washington PA |  |  |  |  | Harlingen |  |  | Newport News | Spokane |  | Rice Lake |  |  |  |  | Packaged VAV with electric reheat | PVAV_Elec
| Kentucky |  | Hoonah |  |  | Hawthorne | Lakewood |  |  | Orlando | [5 empty] | Fairfield IA | Topeka | [5 empty] | Kingsford | Faribault |  |  |  | North Platte |  |  |  |  | Wappingers Falls | Wilmington NC |  |  |  |  | Williamsport |  |  |  |  | Hondo |  |  | Norfolk VA | Stampede Pass |  | Sturgeon Bay |  |  |  |  | Packaged VAV with hydronic reheat | PVAV
| Louisiana |  | Hooper Bay |  |  | Hayward | Lamar |  |  | Panama City | [5 empty] | Fort Dodge | Wichita | [5 empty] | Lansing | Fergus Falls |  |  |  | Omaha |  |  |  |  | Watertown NY | Winston-Salem | [9 empty] | Houston |  |  | Petersburg VA | Tacoma |  | Watertown WI |  |  |  |  | Built-up VAV with hydronic reheat | VAV
| Maine |  | Huslia |  |  | Imperial CA | Leadville |  |  | Pensacola | [5 empty] | Fort Madison | [6 empty] | Manistee | Flying Cloud |  |  |  | O'Neill |  |  |  |  | Westhampton Beach | [10 empty] | Killeen |  |  | Pulaski | The Dalles |  | Wausau |  |  |  |  | Central Ducted VAV | VAV
| Maryland |  | Iliamna |  |  | Lancaster CA | Limon |  |  | Sarasota | [5 empty] | Keokuk | [6 empty] | Marie | Fosston |  |  |  | Ord |  |  |  |  | White Plains | [10 empty] | Kingsville |  |  | Quantico | Toledo WA | [6 empty] | PTAC | PTAC
| Massachusetts |  | Juneau |  |  | Lemoore | Montrose |  |  | St. Petersburg | [5 empty] | Knoxville IA | [6 empty] | Menominee | Glenwood |  |  |  | Scottsbluff | [15 empty] | Laredo |  |  | Richmond | Walla Walla | [6 empty] | PTHP | PTHP
| Michigan |  | Kake |  |  | Livermore | Pueblo |  |  | Tallahasse | [5 empty] | Le Mars | [6 empty] | Mount Clemens | Grand Rapids MN |  |  |  | Sidney NE | [15 empty] | Longview |  |  | Roanoke | Wenatchee | [6 empty] | Fan Coil Unit | FCU
| Minnesota |  | Kenai |  |  | Lompoc | Rifle |  |  | Tampa | [5 empty] | Mason City | [6 empty] | Muskegon | Hallock |  |  |  | Tekamah | [15 empty] | Lubbock |  |  | Virginia Beach | Whidbey Island | [6 empty] | Other | FCU
| Mississippi |  | Ketchikan |  |  | Long Beach | Trinidad |  |  | Vero Beach | [5 empty] | Monticello IA | [6 empty] | Oscoda | Hibbing |  |  |  | Valentine | [15 empty] | Lufkin |  |  | Weyers Cave | Yakima
| Missouri |  | King Salmon |  |  | Los Angeles |  |  |  | West Palm Beach | [5 empty] | Muscatine | [6 empty] | Pellston | Hutchinson | [19 empty] | Marfa |  |  | Winchester
| Montana |  | Kodiak |  |  | McKinleyville | [9 empty] | Newton IA | [6 empty] | Port Huron | International Falls | [19 empty] | McAllen |  |  | Wise | [7 empty] | HVAC Type, Hospital
| Nebraska |  | Mekoryuk |  |  | Merced | [9 empty] | Oelwen | [6 empty] | Traverse City | Litchfield | [19 empty] | McGregor | [10 empty] | Central Ducted VAV | VAV
| Nevada |  | Middleton Island |  |  | Modesto | [9 empty] | Orange City | [6 empty] | Waterford Township | Little Falls | [19 empty] | Midland | [10 empty] | Other | VAV
| New_Hampshire |  | Palmer |  |  | Montague | [9 empty] | Ottumwa | [7 empty] | Mankato | [19 empty] | Mineral wells
| New_Jersey |  | Petersburg AK |  |  | Monterey | [9 empty] | Red Oak | [7 empty] | Marshall | [19 empty] | Nacogdockes | [10 empty] | HVAC Type, Mid-rise Multi-family
| New_Mexico |  | Point Heiden |  |  | Napa | [9 empty] | Sheldon | [7 empty] | Minneapolis | [19 empty] | Palacios | [10 empty] | Fan Coil Unit
| New_York |  | Saint Mary's |  |  | Needles | [9 empty] | Shenandoah | [7 empty] | Mora | [19 empty] | Paris | [10 empty] | Other
| North_Carolina |  | Sand Point |  |  | Oakland | [9 empty] | Sioux City | [7 empty] | Morris | [19 empty] | Port Arthur
| North_Dakota |  | Seward |  |  | Oxnard | [9 empty] | Spencer | [7 empty] | New Ulm | [19 empty] | Rockport | [10 empty] | HVAC Type, Low-rise Multi-family
| Ohio |  | Sitka Japonski |  |  | Palm Springs | [9 empty] | Storm Lake | [7 empty] | Orr | [19 empty] | San Angelo | [10 empty] | PTAC
| Oklahoma |  | Skagway |  |  | Palmdale | [9 empty] | Washington IA | [7 empty] | Owatonna | [19 empty] | San Antonio | [10 empty] | Other
| Oregon |  | Soldotna |  |  | Paso Robles | [9 empty] | Waterloo | [7 empty] | Park Rapids | [19 empty] | Temple
| Pennsylvania |  | St. Paul |  |  | Porterville | [9 empty] | Webster City | [7 empty] | Pipestone | [19 empty] | Tyler
| Rhode_Island |  | Talkeetna |  |  | Red Bluff | [17 empty] | Red Wing | [19 empty] | Victoria
| South_Carolina |  | Togiac |  |  | Redding | [17 empty] | Redwood Falls | [19 empty] | Waco
| South_Dakota |  | Utqiagvik |  |  | Ridgecrest | [17 empty] | Rochester | [19 empty] | Wichita Falls
| Tennessee |  | Valdez |  |  | Riverside | [17 empty] | Roseau | [19 empty] | Wink
| Texas |  | Whittier |  |  | Sacremento | [17 empty] | Silver Bay
| Utah |  | Wrangell |  |  | Salinas | [17 empty] | St Cloud
| Vermont |  | Yakutat |  |  | San Diego | [17 empty] | St Paul
| Virginia |  |  |  |  | San Francisco | [17 empty] | Thief River Falls
| Washington |  |  |  |  | San Jose | [17 empty] | Two Harbors
| West_Virginia |  |  |  |  | San Luis Obispo | [17 empty] | Wheaton
| Wisconsin |  |  |  |  | Sandberg | [17 empty] | Willmar
| Wyoming |  |  |  |  | Santa Anna | [17 empty] | Winona
[6 empty] | Santa Barbara | [17 empty] | Worthington
Santa Maria
Santa Monica
Santa Rose
South Lake Tahoe
Stockton
Truckee
Twentynine Palms
Ukiah
Van Nuys
Visalia
Yuba City

## Weather Information (hidden)
Cities | Heating Degree Days (HDD) | Cooling Degree Days (CDD)
Anniston | 2585 | 1713 | Alabama |  | State | City | HDD | CDD | State | City | HDD | CDD | State | City | HDD | CDD
Auburn AL | 2688 | 1477 |  |  | Alabama | Anniston | 2585 | 1713 | Arkansas | Batesville | 3761 | 1687 |  | Stockton | 2494 | 1296
Birmingham | 2698 | 1912 |  |  |  | Auburn AL | 2688 | 1477 |  | Bentonville | 4394 | 1514 |  | Truckee | 7884 | 87
Daleville | 2447 | 2122 |  |  |  | Birmingham | 2698 | 1912 |  | El Dorado | 2672 | 2512 |  | Twentynine Palms | 1788 | 3297
Dothan | 2072 | 2443 |  |  |  | Daleville | 2447 | 2122 |  | Fayetteville AR | 3726 | 1753 |  | Ukiah | 2981 | 874
Gadsen | 3063 | 1383 |  |  |  | Dothan | 2072 | 2443 |  | Flippin | 3724 | 1604 |  | Van Nuys | 1214 | 1507
Huntsville | 3472 | 1701 |  |  |  | Gadsen | 3063 | 1383 |  | Fort Smith | 3596 | 2020 |  | Visalia | 3032 | 1602
Mobile | 1724 | 2524 |  |  |  | Huntsville | 3472 | 1701 |  | Harrison | 3822 | 1590 |  | Yuba City | 2533 | 1476
Montgomery | 2183 | 2124 |  |  |  | Mobile | 1724 | 2524 |  | Hot Springs AR | 3256 | 2111 | Colorado | Akron CO | 6087 | 823
Muscle Shoals | 2788 | 1701 |  |  |  | Montgomery | 2183 | 2124 |  | Jonesboro | 4240 | 1934 |  | Alamosa | 8528 | 23
Troy | 2196 | 2217 |  |  |  | Muscle Shoals | 2788 | 1701 |  | Little Rock | 3079 | 2076 |  | Aspen | 8294 | 68
Tuscaloosa | 2656 | 2101 |  |  |  | Troy | 2196 | 2217 |  | Pine Bluff | 3384 | 2460 |  | Aurora CO | 6093 | 825
Adak | 9202 | 0 | Aklaska |  |  | Tuscaloosa | 2656 | 2101 |  | Rogers | 4327 | 1669 |  | Broomfield | 5836 | 637
Anchorage | 10158 | 0 |  |  | Aklaska | Adak | 9202 | 0 |  | Siloam Spring | 3868 | 1637 |  | Colorado Springs | 6115 | 481
Aniak | 11513 | 0 |  |  |  | Anchorage | 10158 | 0 |  | Springdale | 3963 | 1480 |  | Cortez | 5921 | 523
Annette Island | 6865 | 11 |  |  |  | Aniak | 11513 | 0 |  | Stuttgart | 2833 | 2120 |  | Craig | 8497 | 74
Anvik | 11628 | 27 |  |  |  | Annette Island | 6865 | 11 |  | Texarkana | 2471 | 2486 |  | Denver | 5655 | 923
Big River Lakes | 9868 | 1 |  |  |  | Anvik | 11628 | 27 |  | Walnut Ridge | 3733 | 1731 |  | Durango | 7114 | 312
Birchwood | 9521 | 1 |  |  |  | Big River Lakes | 9868 | 1 | California | Alturas | 6458 | 320 |  | Fort Collins | 7048 | 509
Chulitna | 10471 | 3 |  |  |  | Birchwood | 9521 | 1 |  | Bakersfield | 2013 | 2240 |  | Grand Junction | 5283 | 1230
Cold Bay | 9517 | 0 |  |  |  | Chulitna | 10471 | 3 |  | Bishop | 4053 | 1087 |  | Greeley | 6792 | 484
Cordova | 9376 | 0 |  |  |  | Cold Bay | 9517 | 0 |  | Blue Canyon | 5176 | 465 |  | Gunnison | 9306 | 13
Dillingham | 10504 | 1 |  |  |  | Cordova | 9376 | 0 |  | Blythe | 826 | 4527 |  | Gypsum | 7853 | 116
Dutch Harbor | 8963 | 0 |  |  |  | Dillingham | 10504 | 1 |  | Burbank | 1437 | 1449 |  | Hayden | 8169 | 211
Emmonak | 11775 | 0 |  |  |  | Dutch Harbor | 8963 | 0 |  | Camarillo | 1979 | 342 |  | La Junta | 5194 | 1318
Fairbanks | 13072 | 31 |  |  |  | Emmonak | 11775 | 0 |  | Camp Pendleton | 2499 | 731 |  | Lakewood | 6112 | 582
Gustavus | 9123 | 0 |  |  |  | Fairbanks | 13072 | 31 |  | Carlsbad CA | 1798 | 272 |  | Lamar | 5635 | 1305
Healy | 10689 | 0 |  |  |  | Gustavus | 9123 | 0 |  | Chino | 1609 | 1330 |  | Leadville | 10266 | 0
Homer | 9696 | 0 |  |  |  | Healy | 10689 | 0 |  | Chula Vista | 1642 | 410 |  | Limon | 6576 | 373
Hoonah | 8858 | 0 |  |  |  | Homer | 9696 | 0 |  | Concord CA | 2484 | 785 |  | Montrose | 5984 | 746
Hooper Bay | 11970 | 0 |  |  |  | Hoonah | 8858 | 0 |  | Crescent City | 4884 | 0 |  | Pueblo | 5178 | 936
Huslia | 13574 | 0 |  | ??? |  | Hooper Bay | 11970 | 0 |  | Daggett | 1931 | 3036 |  | Rifle | 5943 | 631
Iliamna | 9855 | 8 |  |  |  | Huslia | 13574 | 0 |  | Fairfield CA | 2708 | 1313 |  | Trinidad | 5266 | 798
Juneau | 8471 | 1 |  |  |  | Iliamna | 9855 | 8 |  | Fresno | 2327 | 2101 | Connecticut | Danbury | 6218 | 503
Kake | 8385 | 0 |  |  |  | Juneau | 8471 | 1 |  | Fullerton | 1312 | 1187 |  | Groton | 5700 | 418
Kenai | 10071 | 5 |  |  |  | Kake | 8385 | 0 |  | Hawthorne | 1299 | 570 |  | Hartford Brainard | 5969 | 731
Ketchikan | 8033 | 22 |  |  |  | Kenai | 10071 | 5 |  | Hayward | 2327 | 131 |  | New Haven | 5524 | 625
King Salmon | 10754 | 2 |  |  |  | Ketchikan | 8033 | 22 |  | Imperial CA | 837 | 4228 |  | Oxford | 6425 | 551
Kodiak | 8551 | 5 |  |  |  | King Salmon | 10754 | 2 |  | Lancaster CA | 2871 | 1983 |  | Stratford | 5530 | 738
Mekoryuk | 11572 | 0 |  |  |  | Kodiak | 8551 | 5 |  | Lemoore | 1654 | 1754 | Delaware | Dover | 4987 | 1010
Middleton Island | 8285 | 0 |  |  |  | Mekoryuk | 11572 | 0 |  | Livermore | 2933 | 679 |  | Wilmington DE | 5087 | 1088
Palmer | 8599 | 4 |  |  |  | Middleton Island | 8285 | 0 |  | Lompoc | 3256 | 27 | Florida | Crestview | 1672 | 2354
Petersburg AK | 8490 | 6 |  |  |  | Palmer | 8599 | 4 |  | Long Beach | 1136 | 995 |  | Daytona | 789 | 2857
Port Heiden | 10084 | 0 |  |  |  | Petersburg AK | 8490 | 6 |  | Los Angeles | 1283 | 617 |  | Fort Lauderdale | 322 | 4114
Saint Mary's | 11770 | 0 |  |  |  | Port Heiden | 10084 | 0 |  | McKinleyville | 4964 | 4 |  | Fort Myers | 205 | 4113
Sand Point | 9143 | 0 |  |  |  | Saint Mary's | 11770 | 0 |  | Merced | 2268 | 1389 |  | Fort Pierce | 722 | 2959
Seward | 9112 | 0 |  |  |  | Sand Point | 9143 | 0 |  | Modesto | 2211 | 1445 |  | Gainesville | 1306 | 2659
Sitka Japonski | 8002 | 0 |  |  |  | Seward | 9112 | 0 |  | Montague | 5097 | 567 |  | Homestead | 318 | 4117
Skagway | 8379 | 9 |  |  |  | Sitka Japonski | 8002 | 0 |  | Monterey | 3218 | 64 |  | Jacksonville FL | 1281 | 2565
Soldotna | 10146 | 3 |  |  |  | Skagway | 8379 | 9 |  | Napa | 3186 | 191 |  | Key West | 67 | 4906
St. Paul | 10607 | 0 |  |  |  | Soldotna | 10146 | 3 |  | Needles | 944 | 4672 |  | Lakeland | 973 | 3374
Talkeetna | 10973 | 2 |  |  |  | St. Paul | 10607 | 0 |  | Oakland | 2816 | 128 |  | Marathon | 124 | 5280
Togiac | 10391 | 3 |  |  |  | Talkeetna | 10973 | 2 |  | Oxnard | 2010 | 186 |  | Mayport | 1037 | 2806
Utqiagvik | 9862 | 0 |  |  |  | Togiac | 10391 | 3 |  | Palm Springs | 668 | 4333 |  | Melbourne | 369 | 3269
Valdez | 9257 | 0 |  |  |  | Utqiagvik | 9862 | 0 |  | Palmdale | 2829 | 1947 |  | Miami | 150 | 4292
Whittier | 9362 | 1 |  |  |  | Valdez | 9257 | 0 |  | Paso Robles | 2558 | 852 |  | Milton | 1728 | 2305
Wrangell | 7985 | 5 |  |  |  | Whittier | 9362 | 1 |  | Porterville | 2465 | 1620 |  | Naples | 289 | 3443
Yakutat | 9117 | 0 |  |  |  | Wrangell | 7985 | 5 |  | Red Bluff | 2782 | 1868 |  | Ocala | 1144 | 2724
Casa Granda | 1473 | 3715 | Arizona |  |  | Yakutat | 9117 | 0 |  | Redding | 2694 | 1688 |  | Orlando | 526 | 3234
Douglas | 2328 | 1832 |  |  | Arizona | Casa Granda | 1473 | 3715 |  | Ridgecrest | 2782 | 3004 |  | Panama City | 1269 | 2877
Flagstaff | 7112 | 110 |  |  |  | Douglas | 2328 | 1832 |  | Riverside | 1609 | 1413 |  | Pensacola | 1174 | 2711
Grand Canyon | 6605 | 93 |  |  |  | Flagstaff | 7112 | 110 |  | Sacremento | 2581 | 1281 |  | Sarasota | 604 | 3266
Kingman | 3005 | 2444 |  |  |  | Grand Canyon | 6605 | 93 |  | Salinas | 2852 | 84 |  | St. Petersburg | 429 | 3824
Luke | 1137 | 4152 |  |  |  | Kingman | 3005 | 2444 |  | San Diego | 1019 | 742 |  | Tallahasse | 1545 | 2370
Page | 3658 | 1967 |  |  |  | Luke | 1137 | 4152 |  | San Francisco | 2737 | 97 |  | Tampa | 646 | 3442
Phoenix | 997 | 4591 |  |  |  | Page | 3658 | 1967 |  | San Jose | 2301 | 395 |  | Valparaiso | 2072 | 2339
Prescott | 4146 | 1037 |  |  |  | Phoenix | 997 | 4591 |  | San Luis Obispo | 2325 | 201 |  | Vero Beach | 299 | 3489
Safford | 1891 | 2760 |  |  |  | Prescott | 4146 | 1037 |  | Sandberg | 3610 | 1089 |  | West Palm Beach | 316 | 3787
Scottsdale | 1214 | 4065 |  |  |  | Safford | 1891 | 2760 |  | Santa Anna | 1106 | 657 | Georgia | Albany GA | 1739 | 2456
Show Low | 4515 | 643 |  |  |  | Scottsdale | 1214 | 4065 |  | Santa Barbara | 2433 | 104 |  | Alma | 2097 | 2316
Tucson | 1596 | 3020 |  |  |  | Show Low | 4515 | 643 |  | Santa Maria | 2795 | 32 |  | Athens | 2730 | 1702
Winslow | 4435 | 1247 |  |  |  | Tucson | 1596 | 3020 |  | Santa Monica | 1388 | 467 |  | Atlanta | 2773 | 1809
Yuma | 535 | 4532 |  |  |  | Winslow | 4435 | 1247 |  | Santa Rose | 2859 | 329 |  | Augusta GA | 2512 | 2023
Batesville | 3761 | 1687 | Arkansas |  |  | Yuma | 535 | 4532 |  | South Lake Tahoe | 7847 | 11 |  | Brunswick GA | 2102 | 2568
Bentonville | 4394 | 1514
El Dorado | 2672 | 2512 |  |  | State | City | HDD | CDD | State | City | HDD | CDD | State | City | HDD | CDD
Fayetteville AR | 3726 | 1753 |  |  |  | Columbus GA | 2063 | 2407 |  | Fairfield IA | 6031 | 1093 |  | Millinocket | 7921 | 323
Flippin | 3724 | 1604 |  |  |  | Macon | 2400 | 2182 |  | Fort Dodge | 7177 | 825 |  | Portland ME | 7679 | 335
Fort Smith | 3596 | 2020 |  |  |  | Marietta | 3734 | 1401 |  | Fort Madison | 5277 | 1148 |  | Presque Isle | 9295 | 168
Harrison | 3822 | 1590 |  |  |  | Rome | 3331 | 1895 |  | Keokuk | 5496 | 1208 |  | Rockland | 7451 | 194
Hot Springs AR | 3256 | 2111 |  |  |  | Savannah | 1759 | 2474 |  | Knoxville IA | 5891 | 1265 |  | Sanford | 7774 | 259
Jonesboro | 4240 | 1934 |  |  |  | Valdosta | 1525 | 2860 |  | Le Mars | 6122 | 871 |  | Waterville | 7926 | 367
Little Rock | 3079 | 2076 |  |  |  | Warner Robins | 2983 | 2069 |  | Mason City | 7927 | 639 |  | Wiscasset | 6877 | 350
Pine Bluff | 3384 | 2460 |  |  | Hawaii | Hilo | 0 | 3279 |  | Monticello IA | 6857 | 744 | Maryland | Baltimore | 4631 | 1237
Rogers | 4327 | 1669 |  |  |  | Honolulu | 0 | 4561 |  | Muscatine | 6206 | 1026 |  | Camp Springs | 4652 | 1178
Siloam Spring | 3868 | 1637 |  |  |  | Kahului | 0 | 3999 |  | Newton IA | 6207 | 816 |  | Hagerstown | 4867 | 1079
Springdale | 3963 | 1480 |  |  |  | Kalaoa | 0 | 4325 |  | Oelwen | 6483 | 644 |  | Lexington Park | 3556 | 1404
Stuttgart | 2833 | 2120 |  |  |  | Kaneohe | 0 | 4485 |  | Orange City | 6867 | 865 |  | Salisbury | 3910 | 1229
Texarkana | 2471 | 2486 |  |  |  | Kapalua | 0 | 3908 |  | Ottumwa | 6647 | 875 | Massachusetts | Beverly | 6669 | 492
Walnut Ridge | 3733 | 1731 |  |  |  | Kapolei | 12 | 4410 |  | Red Oak | 5959 | 1203 |  | Boston | 5793 | 734
Alturas | 6458 | 320 | California |  |  | Lanai | 22 | 2590 |  | Sheldon | 6939 | 723 |  | Chicopee Falls | 6354 | 507
Bakersfield | 2013 | 2240 |  |  |  | Lihue | 0 | 3919 |  | Shenandoah | 6233 | 1258 |  | Hyannis | 5749 | 436
Bishop | 4053 | 1087 |  |  |  | Molokai | 97 | 3734 |  | Sioux City | 6796 | 936 |  | Lawrence | 5940 | 559
Blue Canyon | 5176 | 465 |  |  | Idaho | Boise | 5395 | 756 |  | Spencer | 8206 | 592 |  | Marthas Vineyard | 5622 | 361
Blythe | 826 | 4527 |  |  |  | Burley | 6225 | 927 |  | Storm Lake | 6982 | 821 |  | Mashpee | 6062 | 565
Burbank | 1437 | 1449 |  |  |  | Caldwell | 5803 | 636 |  | Washington IA | 6249 | 991 |  | Nantucket | 5350 | 298
Camarillo | 1979 | 342 |  |  |  | Coeur d'Alene | 6897 | 344 |  | Waterloo | 7257 | 827 |  | New Bedford | 5724 | 577
Camp Pendleton | 2499 | 731 |  |  |  | Grand View | 6105 | 834 |  | Webster City | 6376 | 1099 |  | North Adams | 6626 | 319
Carlsbad CA | 1798 | 272 |  |  |  | Hailey | 7160 | 679 | Kansas | Chanute | 4458 | 1804 |  | Norwood | 6177 | 637
Chino | 1609 | 1330 |  |  |  | Idaho Falls | 7769 | 246 |  | Concordia | 4890 | 1632 |  | Plymouth | 5889 | 374
Chula Vista | 1642 | 410 |  |  |  | Lewiston | 5457 | 885 |  | Dodge City | 4969 | 1457 |  | Provincetown | 5705 | 595
Concord CA | 2484 | 785 |  |  |  | Malad City | 6681 | 546 |  | Emporia | 5717 | 1458 |  | Westfield | 6623 | 494
Crescent City | 4884 | 0 |  |  |  | Pocatello | 7100 | 393 |  | Garden City | 5180 | 1240 |  | Worchester | 7164 | 346
Daggett | 1931 | 3036 |  |  |  | Salmon | 7482 | 309 |  | Goodland | 5915 | 915 | Michigan | Alpena | 8250 | 290
Fairfield CA | 2708 | 1313 |  |  |  | Soda Springs | 8439 | 198 |  | Great Bend | 4891.5 | 1417 |  | Ann Arbor | 6487 | 492
Fresno | 2327 | 2101 |  |  |  | Twin Falls | 6148 | 733 |  | Hays | 5021 | 1558 |  | Battle Creek | 6210 | 639
Fullerton | 1312 | 1187 |  |  | Illinois | Aurora IL | 6790 | 683 |  | Hill City | 5597 | 1192 |  | Benton Harbor | 6588 | 810
Hawthorne | 1299 | 570 |  |  |  | Belleville | 5320 | 1245 |  | Hutchinson KS | 4591 | 1552 |  | Cadillac | 7905 | 373
Hayward | 2327 | 131 |  |  |  | Bloomington IL | 6112 | 847 |  | Junction City | 4528 | 1600 |  | Calumet | 8988 | 239
Imperial CA | 837 | 4228 |  |  |  | Bondville | 5747 | 1021 |  | Liberal | 4810 | 1410 |  | Detroit | 6621 | 679
Lancaster CA | 2871 | 1983 |  |  |  | Chicago | 6399 | 830 |  | Manhattan | 5013 | 1652 |  | Escanaba | 8796 | 131
Lemoore | 1654 | 1754 |  |  |  | Decatur | 5546 | 1166 |  | Newton KS | 5023 | 1400 |  | Flint | 6977 | 515
Livermore | 2933 | 679 |  |  |  | Marion IL | 4674 | 1330 |  | Olathe | 4598 | 1437 |  | Freeland | 7059 | 524
Lompoc | 3256 | 27 |  |  |  | Moline | 6459 | 980 |  | Russell | 5005 | 1436 |  | Grand Rapids MI | 6908 | 579
Long Beach | 1136 | 995 |  |  |  | Mount Vernon | 4817 | 1412 |  | Salina | 4660 | 1787 |  | Houghton Lake | 8067 | 316
Los Angeles | 1283 | 617 |  |  |  | Murphysboro | 4380 | 1633 |  | Topeka | 4953 | 1315 |  | Howell | 6295 | 899
McKinleyville | 4964 | 4 |  |  |  | Peoria | 6229 | 888 |  | Wichita | 4324 | 1554 |  | Ironwood | 9090 | 348
Merced | 2268 | 1389 |  |  |  | Quincy | 5233 | 1067 | Kentucky | Bowling Green | 4380 | 1410 |  | Jackson MI | 6385 | 715
Modesto | 2211 | 1445 |  |  |  | Rock Falls | 6269 | 785 |  | Fort Knox | 4918 | 1283 |  | Kalamazoo | 6196 | 599
Montague | 5097 | 567 |  |  |  | Rockford | 7237 | 778 |  | Hebron | 5288 | 962 |  | Kincheloe | 9193 | 115
Monterey | 3218 | 64 |  |  |  | Springfield IL | 5527 | 1166 |  | Henderson City | 5049 | 995 |  | Kingsford | 8327 | 432
Napa | 3186 | 191 |  |  |  | West Chicago | 6194 | 830 |  | Hopkinsville | 4484 | 1620 |  | Lansing | 7045 | 597
Needles | 944 | 4672 |  |  | Indiana | Bloomington IN | 5385 | 1025 |  | Jackson KY | 3869 | 1098 |  | Manistee | 7343 | 582
Oakland | 2816 | 128 |  |  |  | Evansville | 4474 | 1376 |  | Lexington | 4856 | 1104 |  | Marie | 9162 | 113
Oxnard | 2010 | 186 |  |  |  | Fort Wayne | 6471 | 764 |  | London | 4529 | 988 |  | Menominee | 7783 | 452
Palm Springs | 668 | 4333 |  |  |  | Huntingburg | 4223 | 1448 |  | Louisville | 4521 | 1449 |  | Mount Clemens | 6040 | 597
Palmdale | 2829 | 1947 |  |  |  | Indianapolis | 5845 | 1044 |  | Somerset | 3916 | 1550 |  | Muskegon | 7018 | 502
Paso Robles | 2558 | 852 |  |  |  | Kokomo | 5957 | 822 |  | West Paducah | 3811 | 1439 |  | Oscoda | 7315 | 455
Porterville | 2465 | 1620 |  |  |  | Lafayette IN | 5967 | 971 | Louisiana | Alexandria LA | 1136 | 2477 |  | Pellston | 7426 | 360
Red Bluff | 2782 | 1868 |  |  |  | Muncie | 5626 | 1004 |  | Baton Rouge | 1762 | 2622 |  | Port Huron | 6522 | 705
Redding | 2694 | 1688 |  |  |  | South Bend | 5956 | 860 |  | Bossier City | 2562 | 2270 |  | Traverse City | 7754 | 370
Ridgecrest | 2782 | 3004 |  |  |  | Terre Haute | 5135 | 1290 |  | Houma | 1677 | 2848 |  | Waterford Township | 6152 | 772
Riverside | 1609 | 1413 |  |  | Iowa | Algona | 6847 | 707 |  | Lafayette LA | 1590 | 2699 | Minnesota | Aitkin | 9304 | 194
Sacremento | 2581 | 1281 |  |  |  | Atlantic | 6656 | 865 |  | Lake Charles | 1635 | 2596 |  | Albert Lea | 7196 | 920
Salinas | 2852 | 84 |  |  |  | Boone | 6699 | 897 |  | Leesville | 2197 | 2514 |  | Alexandria MN | 8895 | 535
San Diego | 1019 | 742 |  |  |  | Burlington IA | 5680 | 1465 |  | Monroe | 2229 | 2270 |  | Austin MN | 7892 | 529
San Francisco | 2737 | 97 |  |  |  | Carroll | 6880 | 899 |  | New Iberia | 1717 | 2559 |  | Baudette | 8804 | 112
San Jose | 2301 | 395 |  |  |  | Cedar Rapids | 6900 | 714 |  | New Orleans | 1358 | 2784 |  | Bemidji | 9161 | 333
San Luis Obispo | 2325 | 201 |  |  |  | Chariton | 6028 | 1252 |  | Patterson | 1452 | 2571 |  | Benson | 8676 | 659
Sandberg | 3610 | 1089 |  |  |  | Charles City | 6765 | 733 |  | Pineville | 2109 | 2421 |  | Brainerd | 8713 | 322
Santa Anna | 1106 | 657 |  |  |  | Clarinda | 6072 | 1319 |  | Shreveport | 2351 | 2384 |  | Cambridge | 8823 | 405
Santa Barbara | 2433 | 104 |  |  |  | Clinton IA | 6895 | 1019 | Maine | Auburn ME | 7691 | 303 |  | Cloquet | 9368 | 258
Santa Maria | 2795 | 32 |  |  |  | Council Bluffs | 5864 | 969 |  | Augusta ME | 7495 | 396 |  | Crane Lake | 10240 | 164
Santa Monica | 1388 | 467 |  |  |  | Creston | 6150 | 983 |  | Bangor | 7671 | 450 |  | Crookston | 9095 | 348
Santa Rose | 2859 | 329 |  |  |  | Decorah | 6125 | 978 |  | Bar Harbor | 8037 | 71 |  | Detroit Lakes | 8704 | 460
South Lake Tahoe | 7847 | 11 |  |  |  | Denison | 6571 | 1057 |  | Brunswick ME | 7456 | 373 |  | Duluth | 9620 | 159
Stockton | 2494 | 1296 |  |  |  | Des Moines | 6493 | 1121 |  | Caribou | 9841 | 171 |  | Ely | 9501 | 186
Truckee | 7884 | 87 |  |  |  | Dubuque | 7516 | 525 |  | Frenchville | 9765 | 164 |  | Eveleth | 9987 | 255
Twentynine Palms | 1788 | 3297 |  |  |  | Estherville | 8458 | 551 |  | Houlton | 9255 | 206 |  | Fairmont | 7586 | 652
Ukiah | 2981 | 874
Van Nuys | 1214 | 1507 |  |  | State | City | HDD | CDD | State | City | HDD | CDD | State | City | HDD | CDD
Visalia | 3032 | 1602 |  |  |  | Faribault | 7497 | 504 |  | Livingston | 7111 | 370 |  | Buffalo | 6612 | 468
Yuba City | 2533 | 1476 |  |  |  | Fergus Falls | 7838 | 841 |  | Miles City | 7617 | 648 |  | Elmira | 6449 | 297
Akron CO | 6087 | 823 | Colorado |  |  | Flying Cloud | 7921 | 958 |  | Missoula | 7323 | 269 |  | Glen Falls | 7158 | 481
Alamosa | 8528 | 23 |  |  |  | Fosston | 9746 | 252 |  | Sidney MT | 9396 | 411 |  | Jamestown NY | 7188 | 278
Aspen | 8294 | 68 |  |  |  | Glenwood | 8440 | 528 |  | Wolf Point | 8983 | 249 |  | Massena | 8046 | 376
Aurora CO | 6093 | 825 |  |  |  | Grand Rapids MN | 9137 | 306 | Nebraska | Ainsworth | 6118 | 789 |  | Monticello NY | 7059 | 428
Broomfield | 5836 | 637 |  |  |  | Hallock | 9445 | 460 |  | Alliance | 7026 | 736 |  | New Windsor | 6159 | 756
Colorado Springs | 6115 | 481 |  |  |  | Hibbing | 9987 | 219 |  | Beatrice | 5646 | 1135 |  | New York | 4885 | 1133
Cortez | 5921 | 523 |  |  |  | Hutchinson MN | 8330 | 620 |  | Bellevue | 6309 | 1139 |  | Nigara Falls | 6484 | 602
Craig | 8497 | 74 |  |  |  | International Falls | 10382 | 259 |  | Broken Bow | 6772 | 790 |  | Republic | 4893 | 983
Denver | 5655 | 923 |  |  |  | Litchfield | 7734 | 543 |  | Chadron | 6543 | 812 |  | Rockester | 6518 | 627
Durango | 7114 | 312 |  |  |  | Little Falls | 9240 | 385 |  | Columbus NC | 6670 | 937 |  | Ronkonkoma | 5005 | 983
Fort Collins | 7048 | 509 |  |  |  | Mankato | 7716 | 645 |  | Falls City | 5775 | 1039 |  | Saranac Lake | 9158 | 149
Grand Junction | 5283 | 1230 |  |  |  | Marshall | 7740 | 688 |  | Fremont | 6953 | 935 |  | Syracuse | 6609 | 535
Greeley | 6792 | 484 |  |  |  | Minneapolis | 7783 | 731 |  | Grand Island | 6654 | 1041 |  | Utica | 6974 | 414
Gunnison | 9306 | 13 |  |  |  | Mora | 8665 | 364 |  | Hastings | 6075 | 1108 |  | Wappingers Falls | 6030 | 607
Gypsum | 7853 | 116 |  |  |  | Morris | 8849 | 375 |  | Holdrege | 6510 | 852 |  | Watertown NY | 7496 | 330
Hayden | 8169 | 211 |  |  |  | New Ulm | 7646 | 641 |  | Imperial NE | 5834 | 1024 |  | Westhampton Beach | 5741 | 455
La Junta | 5194 | 1318 |  |  |  | Orr | 10534 | 152 |  | Kearney | 6348 | 843 |  | White Plains | 5783 | 595
Lakewood | 6112 | 582 | check with Devon (Denver Centennial) |  |  | Owatonna | 7788 | 641 |  | Lincoln | 5892 | 1220 | North Carolina | Asheville | 4273 | 817
Lamar | 5635 | 1305 |  |  |  | Park Rapids | 9215 | 236 |  | McCook | 5616 | 1256 |  | Cape Hatteras | 2563 | 1729
Leadville | 10266 | 0 |  |  |  | Pipestone | 8624 | 649 |  | Norfolk NE | 6943 | 986 |  | Charlotte | 3153 | 1675
Limon | 6576 | 373 |  |  |  | Red Wing | 7935 | 761 |  | North Platte | 6556 | 802 |  | Elizabeth City | 2744 | 1760
Montrose | 5984 | 746 |  |  |  | Redwood Falls | 7938 | 609 |  | Omaha | 5954 | 1275 |  | Fayetteville NC | 3489 | 1576
Pueblo | 5178 | 936 |  |  |  | Rochester | 8386 | 488 |  | O'Neill | 7733 | 847 |  | Goldsboro | 3589 | 1743
Rifle | 5943 | 631 |  |  |  | Roseau | 9817 | 162 |  | Ord | 6279 | 872 |  | Greensboro | 3868 | 1371
Trinidad | 5266 | 798 |  |  |  | Silver Bay | 10453 | 59 |  | Scottsbluff | 6560 | 760 |  | Greenville NC | 3040 | 1603
Danbury | 6218 | 503 | Connecticut |  |  | St Cloud | 9020 | 444 |  | Sidney NE | 6864 | 494 |  | Havelock | 3345 | 1701
Groton | 5700 | 418 |  |  |  | St Paul | 8019 | 587 |  | Tekamah | 6650 | 1005 |  | Hickory | 3457 | 1416
Hartford Brainard | 5969 | 731 |  |  |  | Thief River Falls | 9328 | 341 |  | Valentine | 6453 | 811 |  | Jacksonville NC | 3814 | 1370
New Haven | 5524 | 625 |  |  |  | Two Harbors | 9412 | 190 | Nevada | Elko | 7070 | 407 |  | Kinston | 3397 | 1818
Oxford | 6425 | 551 |  |  |  | Wheaton | 8713 | 496 |  | Ely | 7267 | 154 |  | Manteo | 3053 | 1617
Stratford | 5530 | 738 |  |  |  | Willmar | 7649 | 581 |  | Fallon | 5163 | 1010 |  | New Bern | 2276 | 1874
Dover | 4987 | 1010 | Delaware |  |  | Winona | 7711 | 633 |  | Las Vegas NV | 2301 | 3187 |  | Raleigh | 3465 | 1566
Wilmington DE | 5087 | 1088 |  |  |  | Worthington | 7750 | 644 |  | Lovelock | 5351 | 836 |  | Rocky Mount | 2878 | 1435
Crestview | 1672 | 2354 | Florida |  | Mississippi | Biloxi | 1928 | 2606 |  | Mercury | 3001 | 2396 |  | Southern Pines | 3570 | 1496
Daytona | 789 | 2857 |  |  |  | Columbus MS | 3394 | 2077 |  | Reno | 5488 | 620 |  | Wilmington NC | 2401 | 1928
Fort Lauderdale | 322 | 4114 |  |  |  | Greenville MS | 2432 | 2468 |  | Tonopah | 5431 | 747 |  | Winston-Salem | 3214 | 1244
Fort Myers | 205 | 4113 |  |  |  | Greenwood | 2552 | 2164 |  | Winnemucca | 6158 | 567 | North Dakota | Bismarck | 8452 | 453
Fort Pierce | 722 | 2959 |  |  |  | Gulfport | 1619 | 2565 | New Hampshire | Berlin | 8891 | 145 |  | Devils Lake | 9251 | 288
Gainesville | 1306 | 2659 |  |  |  | Hattiesburg | 2274 | 2071 |  | Concord NH | 7479 | 397 |  | Dickinson | 9028 | 417
Homestead | 318 | 4117 |  |  |  | Jackson MS | 2428 | 2237 |  | Keene | 7169 | 470 |  | Fargo | 9211 | 491
Jacksonville FL | 1281 | 2565 |  |  |  | McComb | 2086 | 2315 |  | Laconia | 7198 | 396 |  | Grand Forks | 9534 | 486
Key West | 67 | 4906 |  |  |  | Meridian | 2417 | 2038 |  | Lebanon | 7349 | 389 |  | Jamestown ND | 9505 | 519
Lakeland | 973 | 3374 |  |  |  | Natchez | 1915 | 2060 |  | Manchester | 6322 | 664 |  | Minot | 8972 | 432
Marathon | 124 | 5280 |  |  |  | Starkville | 3378 | 1962 |  | Mount Washington | 13275 | 0 |  | Williston | 8467 | 404
Mayport | 1037 | 2806 |  |  |  | Tupelo | 3039 | 1905 |  | Portsmouth | 6753 | 527 | Ohio | Akron OH | 259 | 654
Melbourne | 369 | 3269 |  |  | Missouri | Cape Girardeau | 4506 | 1289 | New Jersey | Atlantic City | 5073 | 886 |  | Cincinnati | 4911 | 1039
Miami | 150 | 4292 |  |  |  | Columbia MO | 5307 | 1190 |  | Belmar | 5280 | 890 |  | Cleveland | 6160 | 760
Milton | 1728 | 2305 |  |  |  | Farmington MO | 4527 | 1190 |  | Fairfield NJ | 5060 | 654 |  | Columbus OH | 5599 | 747
Naples | 289 | 3443 |  |  |  | Ft. Leonard Wood | 4675 | 1496 |  | Millville | 4680 | 1011 |  | Dayton | 5945 | 905
Ocala | 1144 | 2724 |  |  |  | Jefferson City | 4504 | 1469 |  | Newark | 5057 | 1237 |  | Findlay | 5590 | 541
Orlando | 526 | 3234 |  |  |  | Joplin | 3663 | 1949 |  | Rio Grande | 4286 | 1028 |  | Mansfield | 6615 | 620
Panama City | 1269 | 2877 |  |  |  | Kaiser | 4634 | 1528 |  | Teterboro | 4868 | 695 |  | Toledo OH | 6515 | 610
Pensacola | 1174 | 2711 |  |  |  | Kansas City | 5434 | 1316 |  | Trenton | 5040 | 1177 |  | Youngstown | 6628 | 531
Sarasota | 604 | 3266 |  |  |  | Kirksville | 6397 | 1047 | New Mexico | Alamogordo | 3327 | 1793 |  | Zanesville | 4941 | 702
St. Petersburg | 429 | 3824 |  |  |  | Poplar Bluff | 4108 | 1592 |  | Albuquerque | 4157 | 1269 | Oklahoma | Altus | 3164 | 2563
Tallahasse | 1545 | 2370 |  |  |  | Springfield MO | 4629 | 1307 |  | Carlsbad NM | 2764 | 2298 |  | Bartlesville | 4266 | 1654
Tampa | 646 | 3442 |  |  |  | St. Joseph | 5495 | 1379 |  | Clayton | 4765 | 1156 |  | Clinton OK | 4175 | 2023
Valparaiso | 2072 | 2339 |  |  |  | St. Louis | 4846 | 1555 |  | Clovis | 4467 | 1396 |  | Enid | 4466 | 2034
Vero Beach | 299 | 3489 |  |  |  | Vichy | 4729 | 924 |  | Deming | 2878 | 1891 |  | Fort Sill | 3421 | 2392
West Palm Beach | 316 | 3787 |  |  |  | Warrensburg | 4803 | 1344 |  | Farmington NM | 5199 | 1022 |  | Gage | 4103 | 2013
Albany GA | 1739 | 2456 | Georgia |  | Montana | Billings | 6731 | 548 |  | Gallup | 6002 | 388 |  | Hobart | 3600 | 2377
Alma | 2097 | 2316 |  |  |  | Bozeman | 8354 | 282 |  | Las Cruces | 2876 | 2146 |  | Lawton | 3055 | 1979
Athens | 2730 | 1702 |  |  |  | Butte | 9089 | 101 |  | Las Vegas NM | 5180 | 307 |  | McAlester | 3081 | 2086
Atlanta | 2773 | 1809 |  |  |  | Cut Bank | 8186 | 86 |  | Roswell | 2735 | 1932 |  | Oklahoma City | 3556 | 2038
Augusta GA | 2512 | 2023 |  |  |  | Glasgow | 8163 | 504 |  | Ruidoso | 4095 | 604 |  | Ponca City | 3887 | 2437
Brunswick GA | 2102 | 2568 |  |  |  | Glendive | 8667 | 555 |  | Santa Fe | 5449 | 589 |  | Stillwater | 3799 | 2185
Columbus GA | 2063 | 2407 |  |  |  | Great Falls | 7854 | 344 |  | Taos | 6904 | 198 |  | Tulsa | 3844 | 2066
Macon | 2400 | 2182 |  |  |  | Havre | 8213 | 432 |  | Truth or Consequences | 3102 | 1742 | Oregon | Astoria | 4933 | 48
Marietta | 3734 | 1401 |  |  |  | Helena | 7587 | 320 |  | Tucumcari | 4109 | 1423 |  | Aurora OR | 4277 | 327
Rome | 3331 | 1895 |  |  |  | Kalispell | 7928 | 126 | New York | Albany NY | 6773 | 489 |  | Baker City | 7142 | 231
Savannah | 1759 | 2474 |  |  |  | Lewistown | 8014 | 107 |  | Binghamton | 7015 | 404 |  | Burns | 7201 | 230
Valdosta | 1525 | 2860
Warner Robins | 2983 | 2069 |  |  | State | City | HDD | CDD | State | City | HDD | CDD | State | City | HDD | CDD
Hilo | 0 | 3279 | Hawaii |  |  | Corvallus | 4257 | 405 |  | Del Rio | 1340 | 3187 |  | Weyers Cave | 4878 | 1102
Honolulu | 0 | 4561 |  |  |  | Eugene | 4803 | 295 |  | El Paso | 2499 | 2171 |  | Winchester | 5193 | 1196
Kahului | 0 | 3999 |  |  |  | Klamath Falls | 6765 | 185 |  | Galveston | 1096 | 3116 |  | Wise | 4910 | 747
Kalaoa | 0 | 4325 |  |  |  | La Grande | 6152 | 329 |  | Georgetown | 2070 | 2683 | Washington | Aberdeen WA
Kaneohe | 0 | 4485 |  |  |  | Lakeview | 7091 | 199 |  | Greenville TX | 2717 | 2445 |  | Bellingham | 5768 | 24
Kapalua | 0 | 3908 |  |  |  | Medford | 4530 | 602 |  | Harlingen | 518 | 3816 |  | Bremerton | 5533 | 112
Kapolei | 12 | 4410 |  |  |  | North Bend | 4525 | 0 |  | Hondo | 1694 | 2825 |  | Ephrata | 5578 | 882
Lanai | 22 | 2590 |  |  |  | Pendleton | 5204 | 585 |  | Houston | 1439 | 2974 |  | Everett | 5097 | 69
Lihue | 0 | 3919 |  |  |  | Portland OR | 4187 | 367 |  | Killeen | 2087 | 2721 |  | Forks | 5682 | 19
Molokai | 97 | 3734 |  |  |  | Redmond | 6583 | 204 |  | Kingsville | 895 | 3419 |  | Hanford | 5669 | 1007
Boise | 5395 | 756 | Idaho |  |  | Roseburg | 3798 | 405 |  | Laredo | 1164 | 4080 |  | Hoquiam | 5240 | 21
Burley | 6225 | 927 |  |  |  | Salem | 4583 | 275 |  | Longview | 2131 | 2437 |  | Kelso | 4682 | 115
Caldwell | 5803 | 636 |  |  |  | Sexton Summit | 5657 | 362 |  | Lubbock | 3436 | 1699 |  | Moses Lake | 5431 | 641
Coeur d'Alene | 6897 | 344 |  |  | Pennsylvania | Allentown | 5651 | 773 |  | Lufkin | 1823 | 2479 |  | Olympia | 5331 | 118
Grand View | 6105 | 834 |  |  |  | Altoona | 5917 | 595 |  | Marfa | 3117 | 1044 |  | Pasco | 4921 | 711
Hailey | 7160 | 679 |  |  |  | Bradford | 8204 | 204 |  | McAllen | 729 | 3903 |  | Port Angeles | 5945 | 13
Idaho Falls | 7769 | 246 |  |  |  | Butler | 6575 | 481 |  | McGregor | 2334 | 2614 |  | Pullman | 6483 | 234
Lewiston | 5457 | 885 |  |  |  | DuBois | 6942 | 386 |  | Midland | 2482 | 2057 |  | Renton | 4378 | 216
Malad City | 6681 | 546 |  |  |  | Erie | 6460 | 579 |  | Mineral wells | 2363 | 2495 |  | Seattle | 4372 | 169
Pocatello | 7100 | 393 |  |  |  | Franklin PA | 6830 | 327 |  | Nacogdockes | 2305 | 2313 |  | Spokane | 6716 | 341
Salmon | 7482 | 309 |  |  |  | Harrisburg | 5409 | 927 |  | Palacios | 1346 | 3024 |  | Stampede Pass | 8898 | 81
Soda Springs | 8439 | 198 |  |  |  | Johnstown | 6516 | 482 |  | Paris | 3100 | 2057 |  | Tacoma | 5664 | 142
Twin Falls | 6148 | 733 |  |  |  | Lancaster PA | 4955 | 877 |  | Port Arthur | 1422 | 2904 |  | The Dalles | 4501 | 879
Aurora IL | 6790 | 683 | Illinois |  |  | Middletown | 6105 | 1123 |  | Rockport | 691 | 3576 |  | Toledo WA | 5853 | 82
Belleville | 5320 | 1245 |  |  |  | Philadelphia | 4824 | 1184 |  | San Angelo | 2485 | 2259 |  | Walla Walla | 4836 | 839
Bloomington IL | 6112 | 847 |  |  |  | Pittsburgh | 5925 | 726 |  | San Antonio | 1548 | 2992 |  | Wenatchee | 5748 | 867
Bondville | 5747 | 1021 |  |  |  | Reading | 5067 | 900 |  | Temple | 2260 | 2717 |  | Whidbey Island | 5510 | 0
Chicago | 6399 | 830 |  |  |  | Scranton | 5216 | 608 |  | Tyler | 2339 | 2363 |  | Yakima | 6041 | 430
Decatur | 5546 | 1166 |  |  |  | University Park | 6188 | 585 |  | Victoria | 1309 | 3042 | West Virginia | Beckley | 5361 | 631
Marion IL | 4674 | 1330 |  |  |  | Washington PA | 5727 | 528 |  | Waco | 2251 | 2699 |  | Bluefield | 4451 | 597
Moline | 6459 | 980 |  |  |  | Williamsport | 5761 | 759 |  | Wichita Falls | 2838 | 2350 |  | Bridgeport | 5137 | 855
Mount Vernon | 4817 | 1412 |  |  | Rhode Island | New Shoreham | 5221 | 435 |  | Wink | 2423 | 2932 |  | Charleston WV | 4708 | 1015
Murphysboro | 4380 | 1633 |  |  |  | Pawtucket | 6466 | 504 | Utah | Blanding | 5535 | 1171 |  | Elkins | 6050 | 368
Peoria | 6229 | 888 |  |  |  | Providence | 5870 | 735 |  | Bryce Canyon City | 8955 | 33 |  | Huntington | 4642 | 1077
Quincy | 5233 | 1067 |  |  | South Carolina | Anderson | 3436 | 1037 |  | Cedar City | 5776 | 747 |  | Lewisburg | 6270 | 432
Rock Falls | 6269 | 785 |  |  |  | Beaufort | 2096 | 2158 |  | Delta | 6021 | 799 |  | Martinsburg | 4345 | 761
Rockford | 7237 | 778 |  |  |  | Charleston SC | 2051 | 2302 |  | Hanksville | 5354 | 1445 |  | Morgantown | 5020 | 669
Springfield IL | 5527 | 1166 |  |  |  | Columbia SC | 2593 | 2020 |  | Moab | 5106 | 1301 |  | Parkersburg | 4979 | 1101
West Chicago | 6194 | 830 |  |  |  | Florence | 2316 | 2202 |  | Ogden | 5831 | 1092 |  | Wheeling | 5793 | 639
Bloomington IN | 5385 | 1025 | Indiana |  |  | Greenville SC | 3652 | 1409 |  | Provo | 5836 | 858 | Wisconsin | Antigo | 8664 | 440
Evansville | 4474 | 1376 |  |  |  | Greer | 3244 | 1553 |  | Saint George | 2729 | 2936 |  | Appleton | 7022 | 517
Fort Wayne | 6471 | 764 |  |  |  | Myrtle Beach | 2379 | 1870 |  | Salt Lake City | 5350 | 1118 |  | Eau Claire | 8475 | 600
Huntingburg | 4223 | 1448 |  |  |  | North Myrtle Beach | 2470 | 1727 |  | Vernal | 6661 | 525 |  | Green Bay | 7853 | 496
Indianapolis | 5845 | 1044 |  |  |  | Sumter | 3072 | 1706 |  | Wendover | 5970 | 1221 |  | Janesville | 6713 | 295
Kokomo | 5957 | 822 |  |  | South Dakota | Aberdeen SD | 7968 | 657 | Vermont | Burlington VT | 7491 | 420 |  | La Crosse | 7445 | 748
Lafayette IN | 5967 | 971 |  |  |  | Brookings | 7926 | 449 |  | Montpelier | 7662 | 249 |  | Lone Rock | 6651 | 543
Muncie | 5626 | 1004 |  |  |  | Huron | 8196 | 638 |  | Rutland | 7563 | 485 |  | Madison | 7724 | 604
South Bend | 5956 | 860 |  |  |  | Mitchell | 7879 | 909 |  | Springfield VT | 7264 | 281 |  | Manitowac | 7231 | 322
Terre Haute | 5135 | 1290 |  |  |  | Mobridge | 8474 | 735 | Virginia | Abingdon | 4953 | 1011 |  | Marshfield | 7449 | 432
Algona | 6847 | 707 | Iowa |  |  | Pierre | 7079 | 818 |  | Blacksburg | 5081 | 754 |  | Milwaukee | 7348 | 545
Atlantic | 6656 | 865 |  |  |  | Rapid City | 7203 | 675 |  | Charlottesville | 3697 | 1122 |  | Minocqua | 8772 | 410
Boone | 6699 | 897 |  |  |  | Sioux Falls | 7680 | 680 |  | Danville | 3707 | 1678 |  | Mosinee | 8719 | 401
Burlington IA | 5680 | 1465 |  |  |  | Watertown SD | 8803 | 422 |  | Farmville | 4084 | 1323 |  | Oshkosh | 8013 | 380
Carroll | 6880 | 899 |  |  |  | Yankton | 7058 | 996 |  | Franklin VA | 3096 | 1557 |  | Phillips | 8638 | 337
Cedar Rapids | 6900 | 714 |  |  | Tennessee | Blountville | 4439 | 971 |  | Fredericksburg | 4531 | 1420 |  | Rhinelander | 8823 | 437
Chariton | 6028 | 1252 |  |  |  | Chattanooga | 3224 | 1657 |  | Hampton | 4195 | 1437 |  | Rice Lake | 8706 | 420
Charles City | 6765 | 733 |  |  |  | Crossville | 3976 | 933 |  | Hillsville | 5459 | 604 |  | Sturgeon Bay | 7301 | 424
Clarinda | 6072 | 1319 |  |  |  | Dyersburg | 3723 | 1896 |  | Hot Springs VA | 6585 | 254 |  | Watertown WI | 6864 | 674
Clinton IA | 6895 | 1019 |  |  |  | Jackson TN | 3339 | 1404 |  | Leesburg | 5242 | 1189 |  | Wausau | 7821 | 658
Council Bluffs | 5864 | 969 |  |  |  | Knoxville TN | 3959 | 1482 |  | Lynchburg | 4239 | 1305 | Wyoming | Casper | 7409 | 440
Creston | 6150 | 983 |  |  |  | Memphis | 2999 | 2134 |  | Manassas | 5160 | 935 |  | Cheyenne | 7362 | 265
Decorah | 6125 | 978 |  |  |  | Nashville | 3737 | 1751 |  | Marion VA | 4817 | 744 |  | Cody | 7131 | 436
Denison | 6571 | 1057 |  |  | Texas | Abilene | 2968 | 2302 |  | Martinsville | 4496 | 1133 |  | Evanston | 8339 | 188
Des Moines | 6493 | 1121 |  |  |  | Alice | 912 | 4033 |  | Melfa | 3857 | 1387 |  | Gillette | 6992 | 767
Dubuque | 7516 | 525 |  |  |  | Amarillo | 4130 | 1412 |  | Newport News | 3436 | 1705 |  | Jackson Hole | 9670 | 15
Estherville | 8458 | 551 |  |  |  | Austin TX | 1269 | 2884 |  | Norfolk VA | 3411 | 1630 |  | Lander | 7477 | 432
Fairfield IA | 6031 | 1093 |  |  |  | Brownsville | 750 | 3867 |  | Petersburg VA | 3557 | 1400 |  | Laramie | 7799 | 111
Fort Dodge | 7177 | 825 |  |  |  | Childress | 3258 | 2007 |  | Pulaski | 3336 | 1539 |  | Rawlins | 7392 | 289
Fort Madison | 5277 | 1148 |  |  |  | College Station | 1646 | 2670 |  | Quantico | 4109 | 1232 |  | Riverton | 7579 | 708
Keokuk | 5496 | 1208 |  |  |  | Corpus Christi | 934 | 3313 |  | Richmond | 3883 | 1493 |  | Rock Springs | 7971 | 191
Knoxville IA | 5891 | 1265 |  |  |  | Cotulla | 918 | 3848 |  | Roanoke | 4246 | 1552 |  | Sheridan | 7215 | 399
Le Mars | 6122 | 871 |  |  |  | Dalhart | 5029 | 1041 |  | Virginia Beach | 3336 | 1539 |  | Worland | 7285 | 611
Mason City | 7927 | 639 |  |  | City: Dallas; HDD: 2333; CDD: 2678; City: Washington DC; HDD: 4921; CDD: 1113
Monticello IA | 6857 | 744
Muscatine | 6206 | 1026
Newton IA | 6207 | 816
Oelwen | 6483 | 644
Orange City | 6867 | 865
Ottumwa | 6647 | 875
Red Oak | 5959 | 1203
Sheldon | 6939 | 723
Shenandoah | 6233 | 1258
Sioux City | 6796 | 936
Spencer | 8206 | 592
Storm Lake | 6982 | 821
Washington IA | 6249 | 991
Waterloo | 7257 | 827
Webster City | 6376 | 1099
Chanute | 4458 | 1804 | Kansas
Concordia | 4890 | 1632
Dodge City | 4969 | 1457
Emporia | 5717 | 1458
Garden City | 5180 | 1240
Goodland | 5915 | 915
Great Bend | 4891.5 | 1417
Hays | 5021 | 1558
Hill City | 5597 | 1192
Hutchinson KS | 4591 | 1552
Junction City | 4528 | 1600
Liberal | 4810 | 1410
Manhattan | 5013 | 1652
Newton KS | 5023 | 1400
Olathe | 4598 | 1437
Russell | 5005 | 1436
Salina | 4660 | 1787
Topeka | 4953 | 1315
Wichita | 4324 | 1554
Bowling Green | 4380 | 1410 | Kentucky
Fort Knox | 4918 | 1283
Hebron | 5288 | 962
Henderson City | 5049 | 995
Hopkinsville | 4484 | 1620
Jackson KY | 3869 | 1098
Lexington | 4856 | 1104
London | 4529 | 988
Louisville | 4521 | 1449
Somerset | 3916 | 1550
West Paducah | 3811 | 1439
Alexandria LA | 1136 | 2477 | Louisiana
Baton Rouge | 1762 | 2622
Bossier City | 2562 | 2270
Houma | 1677 | 2848
Lafayette LA | 1590 | 2699
Lake Charles | 1635 | 2596
Leesville | 2197 | 2514
Monroe | 2229 | 2270
New Iberia | 1717 | 2559
New Orleans | 1358 | 2784
Patterson | 1452 | 2571
Pineville | 2109 | 2421
Shreveport | 2351 | 2384
Auburn ME | 7691 | 303 | Maine
Augusta ME | 7495 | 396
Bangor | 7671 | 450
Bar Harbor | 8037 | 71
Brunswick ME | 7456 | 373
Caribou | 9841 | 171
Frenchville | 9765 | 164
Houlton | 9255 | 206
Millinocket | 7921 | 323
Portland ME | 7679 | 335
Presque Isle | 9295 | 168
Rockland | 7451 | 194
Sanford | 7774 | 259
Waterville | 7926 | 367
Wiscasset | 6877 | 350
Baltimore | 4631 | 1237 | Maryland
Camp Springs | 4652 | 1178
Hagerstown | 4867 | 1079
Lexington Park | 3556 | 1404
Salisbury | 3910 | 1229
Beverly | 6669 | 492 | Massachusetts
Boston | 5793 | 734
Chicopee Falls | 6354 | 507
Hyannis | 5749 | 436
Lawrence | 5940 | 559
Marthas Vineyard | 5622 | 361
Mashpee | 6062 | 565
Nantucket | 5350 | 298
New Bedford | 5724 | 577
North Adams | 6626 | 319
Norwood | 6177 | 637
Plymouth | 5889 | 374
Provincetown | 5705 | 595
Westfield | 6623 | 494
Worchester | 7164 | 346
Alpena | 8250 | 290 | Michigan
Ann Arbor | 6487 | 492
Battle Creek | 6210 | 639
Benton Harbor | 6588 | 810
Cadillac | 7905 | 373
Calumet | 8988 | 239
Detroit | 6621 | 679
Escanaba | 8796 | 131
Flint | 6977 | 515
Freeland | 7059 | 524
Grand Rapids MI | 6908 | 579
Houghton Lake | 8067 | 316
Howell | 6295 | 899
Ironwood | 9090 | 348
Jackson MI | 6385 | 715
Kalamazoo | 6196 | 599
Kincheloe | 9193 | 115
Kingsford | 8327 | 432
Lansing | 7045 | 597
Manistee | 7343 | 582
Marie | 9162 | 113
Menominee | 7783 | 452
Mount Clemens | 6040 | 597
Muskegon | 7018 | 502
Oscoda | 7315 | 455
Pellston | 7426 | 360
Port Huron | 6522 | 705
Traverse City | 7754 | 370
Waterford Township | 6152 | 772
Aitkin | 9304 | 194 | Minnesota
Albert Lea | 7196 | 920
Alexandria MN | 8895 | 535
Austin MN | 7892 | 529
Baudette | 8804 | 112
Bemidji | 9161 | 333
Benson | 8676 | 659
Brainerd | 8713 | 322
Cambridge | 8823 | 405
Cloquet | 9368 | 258
Crane Lake | 10240 | 164
Crookston | 9095 | 348
Detroit Lakes | 8704 | 460
Duluth | 9620 | 159
Ely | 9501 | 186
Eveleth | 9987 | 255
Fairmont | 7586 | 652
Faribault | 7497 | 504
Fergus Falls | 7838 | 841
Flying Cloud | 7921 | 958
Fosston | 9746 | 252
Glenwood | 8440 | 528
Grand Rapids MN | 9137 | 306
Hallock | 9445 | 460
Hibbing | 9987 | 219
Hutchinson MN | 8330 | 620
International Falls | 10382 | 259
Litchfield | 7734 | 543
Little Falls | 9240 | 385
Mankato | 7716 | 645
Marshall | 7740 | 688
Minneapolis | 7783 | 731
Mora | 8665 | 364
Morris | 8849 | 375
New Ulm | 7646 | 641
Orr | 10534 | 152
Owatonna | 7788 | 641
Park Rapids | 9215 | 236
Pipestone | 8624 | 649
Red Wing | 7935 | 761
Redwood Falls | 7938 | 609
Rochester | 8386 | 488
Roseau | 9817 | 162
Silver Bay | 10453 | 59
St Cloud | 9020 | 444
St Paul | 8019 | 587
Thief River Falls | 9328 | 341
Two Harbors | 9412 | 190
Wheaton | 8713 | 496
Willmar | 7649 | 581
Winona | 7711 | 633
Worthington | 7750 | 644
Biloxi | 1928 | 2606 | Mississippi
Columbus MS | 3394 | 2077
Greenville MS | 2432 | 2468
Greenwood | 2552 | 2164
Gulfport | 1619 | 2565
Hattiesburg | 2274 | 2071
Jackson MS | 2428 | 2237
McComb | 2086 | 2315
Meridian | 2417 | 2038
Natchez | 1915 | 2060
Starkville | 3378 | 1962
Tupelo | 3039 | 1905
Cape Girardeau | 4506 | 1289 | Missouri
Columbia MO | 5307 | 1190
Farmington MO | 4527 | 1190
Ft. Leonard Wood | 4675 | 1496
Jefferson City | 4504 | 1469
Joplin | 3663 | 1949
Kaiser | 4634 | 1528
Kansas City | 5434 | 1316
Kirksville | 6397 | 1047
Poplar Bluff | 4108 | 1592
Springfield MO | 4629 | 1307
St. Joseph | 5495 | 1379
St. Louis | 4846 | 1555
Vichy | 4729 | 924
Warrensburg | 4803 | 1344
Billings | 6731 | 548 | Montana
Bozeman | 8354 | 282
Butte | 9089 | 101
Cut Bank | 8186 | 86
Glasgow | 8163 | 504
Glendive | 8667 | 555
Great Falls | 7854 | 344
Havre | 8213 | 432
Helena | 7587 | 320
Kalispell | 7928 | 126
Lewistown | 8014 | 107
Livingston | 7111 | 370
Miles City | 7617 | 648
Missoula | 7323 | 269
Sidney MT | 9396 | 411
Wolf Point | 8983 | 249
Ainsworth | 6118 | 789 | Nebraska
Alliance | 7026 | 736
Beatrice | 5646 | 1135
Bellevue | 6309 | 1139
Broken Bow | 6772 | 790
Chadron | 6543 | 812
Columbus NC | 6670 | 937
Falls City | 5775 | 1039
Fremont | 6953 | 935
Grand Island | 6654 | 1041
Hastings | 6075 | 1108
Holdrege | 6510 | 852
Imperial NE | 5834 | 1024
Kearney | 6348 | 843
Lincoln | 5892 | 1220
McCook | 5616 | 1256
Norfolk NE | 6943 | 986
North Platte | 6556 | 802
Omaha | 5954 | 1275
O'Neill | 7733 | 847
Ord | 6279 | 872
Scottsbluff | 6560 | 760
Sidney NE | 6864 | 494
Tekamah | 6650 | 1005
Valentine | 6453 | 811
Elko | 7070 | 407 | Nevada
Ely | 7267 | 154
Fallon | 5163 | 1010
Las Vegas NV | 2301 | 3187
Lovelock | 5351 | 836
Mercury | 3001 | 2396
Reno | 5488 | 620
Tonopah | 5431 | 747
Winnemucca | 6158 | 567
Berlin | 8891 | 145 | New Hampshire
Concord NH | 7479 | 397
Keene | 7169 | 470
Laconia | 7198 | 396
Lebanon | 7349 | 389
Manchester | 6322 | 664
Mount Washington | 13275 | 0
Portsmouth | 6753 | 527
Atlantic City | 5073 | 886 | New Jersey
Belmar | 5280 | 890
Fairfield NJ | 5060 | 654
Millville | 4680 | 1011
Newark | 5057 | 1237
Rio Grande | 4286 | 1028
Teterboro | 4868 | 695
Trenton | 5040 | 1177
Alamogordo | 3327 | 1793 | New Mexico
Albuquerque | 4157 | 1269
Carlsbad NM | 2764 | 2298
Clayton | 4765 | 1156
Clovis | 4467 | 1396
Deming | 2878 | 1891
Farmington NM | 5199 | 1022
Gallup | 6002 | 388
Las Cruces | 2876 | 2146
Las Vegas NM | 5180 | 307
Roswell | 2735 | 1932
Ruidoso | 4095 | 604
Santa Fe | 5449 | 589
Taos | 6904 | 198
Truth or Consequences | 3102 | 1742
Tucumcari | 4109 | 1423
Albany NY | 6773 | 489 | New York
Binghamton | 7015 | 404
Buffalo | 6612 | 468
Elmira | 6449 | 297
Glen Falls | 7158 | 481
Jamestown NY | 7188 | 278
Massena | 8046 | 376
Monticello NY | 7059 | 428
New Windsor | 6159 | 756
New York | 4885 | 1133
Nigara Falls | 6484 | 602
Republic | 4893 | 983
Rockester | 6518 | 627
Ronkonkoma | 5005 | 983
Saranac Lake | 9158 | 149
Syracuse | 6609 | 535
Utica | 6974 | 414
Wappingers Falls | 6030 | 607
Watertown NY | 7496 | 330
Westhampton Beach | 5741 | 455
White Plains | 5783 | 595
Asheville | 4273 | 817 | North Carolina
Cape Hatteras | 2563 | 1729
Charlotte | 3153 | 1675
Elizabeth City | 2744 | 1760
Fayetteville NC | 3489 | 1576
Goldsboro | 3589 | 1743
Greensboro | 3868 | 1371
Greenville NC | 3040 | 1603
Havelock | 3345 | 1701
Hickory | 3457 | 1416
Jacksonville NC | 3814 | 1370
Kinston | 3397 | 1818
Manteo | 3053 | 1617
New Bern | 2276 | 1874
Raleigh | 3465 | 1566
Rocky Mount | 2878 | 1435
Southern Pines | 3570 | 1496
Wilmington NC | 2401 | 1928
Winston-Salem | 3214 | 1244
Bismarck | 8452 | 453 | North Dakota
Devils Lake | 9251 | 288
Dickinson | 9028 | 417
Fargo | 9211 | 491
Grand Forks | 9534 | 486
Jamestown ND | 9505 | 519
Minot | 8972 | 432
Williston | 8467 | 404
Akron OH | 259 | 654 | Ohio
Cincinnati | 4911 | 1039
Cleveland | 6160 | 760
Columbus OH | 5599 | 747
Dayton | 5945 | 905
Findlay | 5590 | 541
Mansfield | 6615 | 620
Toledo OH | 6515 | 610
Youngstown | 6628 | 531
Zanesville | 4941 | 702
Altus | 3164 | 2563 | Oklahoma
Bartlesville | 4266 | 1654
Clinton OK | 4175 | 2023
Enid | 4466 | 2034
Fort Sill | 3421 | 2392
Gage | 4103 | 2013
Hobart | 3600 | 2377
Lawton | 3055 | 1979
McAlester | 3081 | 2086
Oklahoma City | 3556 | 2038
Ponca City | 3887 | 2437
Stillwater | 3799 | 2185
Tulsa | 3844 | 2066
Astoria | 4933 | 48 | Oregon
Aurora OR | 4277 | 327
Baker City | 7142 | 231
Burns | 7201 | 230
Corvallus | 4257 | 405
Eugene | 4803 | 295
Klamath Falls | 6765 | 185
La Grande | 6152 | 329
Lakeview | 7091 | 199
Medford | 4530 | 602
North Bend | 4525 | 0
Pendleton | 5204 | 585
Portland OR | 4187 | 367
Redmond | 6583 | 204
Roseburg | 3798 | 405
Salem | 4583 | 275
Sexton Summit | 5657 | 362
Allentown | 5651 | 773 | Pennsylvania
Altoona | 5917 | 595
Bradford | 8204 | 204
Butler | 6575 | 481
DuBois | 6942 | 386
Erie | 6460 | 579
Franklin PA | 6830 | 327
Harrisburg | 5409 | 927
Johnstown | 6516 | 482
Lancaster PA | 4955 | 877
Middletown | 6105 | 1123
Philadelphia | 4824 | 1184
Pittsburgh | 5925 | 726
Reading | 5067 | 900
Scranton | 5216 | 608
University Park | 6188 | 585
Washington PA | 5727 | 528
Williamsport | 5761 | 759
New Shoreham | 5221 | 435 | Rhode Island
Pawtucket | 6466 | 504
Providence | 5870 | 735
Anderson | 3436 | 1037 | South Carolina
Beaufort | 2096 | 2158
Charleston SC | 2051 | 2302
Columbia SC | 2593 | 2020
Florence | 2316 | 2202
Greenville SC | 3652 | 1409
Greer | 3244 | 1553
Myrtle Beach | 2379 | 1870
North Myrtle Beach | 2470 | 1727
Sumter | 3072 | 1706
Aberdeen SD | 7968 | 657 | South Dakota
Brookings | 7926 | 449
Huron | 8196 | 638
Mitchell | 7879 | 909
Mobridge | 8474 | 735
Pierre | 7079 | 818
Rapid City | 7203 | 675
Sioux Falls | 7680 | 680
Watertown SD | 8803 | 422
Yankton | 7058 | 996
Blountville | 4439 | 971 | Tennessee
Chattanooga | 3224 | 1657
Crossville | 3976 | 933
Dyersburg | 3723 | 1896
Jackson TN | 3339 | 1404
Knoxville TN | 3959 | 1482
Memphis | 2999 | 2134
Nashville | 3737 | 1751
Abilene | 2968 | 2302 | Texas
Alice | 912 | 4033
Amarillo | 4130 | 1412
Austin TX | 1269 | 2884
Brownsville | 750 | 3867
Childress | 3258 | 2007
College Station | 1646 | 2670
Corpus Christi | 934 | 3313
Cotulla | 918 | 3848
Dalhart | 5029 | 1041
Dallas | 2333 | 2678
Del Rio | 1340 | 3187
El Paso | 2499 | 2171
Galveston | 1096 | 3116
Georgetown | 2070 | 2683
Greenville TX | 2717 | 2445
Harlingen | 518 | 3816
Hondo | 1694 | 2825
Houston | 1439 | 2974
Killeen | 2087 | 2721
Kingsville | 895 | 3419
Laredo | 1164 | 4080
Longview | 2131 | 2437
Lubbock | 3436 | 1699
Lufkin | 1823 | 2479
Marfa | 3117 | 1044
McAllen | 729 | 3903
McGregor | 2334 | 2614
Midland | 2482 | 2057
Mineral wells | 2363 | 2495
Nacogdockes | 2305 | 2313
Palacios | 1346 | 3024
Paris | 3100 | 2057
Port Arthur | 1422 | 2904
Rockport | 691 | 3576
San Angelo | 2485 | 2259
San Antonio | 1548 | 2992
Temple | 2260 | 2717
Tyler | 2339 | 2363
Victoria | 1309 | 3042
Waco | 2251 | 2699
Wichita Falls | 2838 | 2350
Wink | 2423 | 2932
Blanding | 5535 | 1171 | Utah
Bryce Canyon City | 8955 | 33
Cedar City | 5776 | 747
Delta | 6021 | 799
Hanksville | 5354 | 1445
Moab | 5106 | 1301
Ogden | 5831 | 1092
Provo | 5836 | 858
Saint George | 2729 | 2936
Salt Lake City | 5350 | 1118
Vernal | 6661 | 525
Wendover | 5970 | 1221
Burlington VT | 7491 | 420 | Vermont
Montpelier | 7662 | 249
Rutland | 7563 | 485
Springfield VT | 7264 | 281
Abingdon | 4953 | 1011 | Virginia
Blacksburg | 5081 | 754
Charlottesville | 3697 | 1122
Danville | 3707 | 1678
Farmville | 4084 | 1323
Franklin VA | 3096 | 1557
Fredericksburg | 4531 | 1420
Hampton | 4195 | 1437
Hillsville | 5459 | 604
Hot Springs VA | 6585 | 254
Leesburg | 5242 | 1189
Lynchburg | 4239 | 1305
Manassas | 5160 | 935
Marion VA | 4817 | 744
Martinsville | 4496 | 1133
Melfa | 3857 | 1387
Newport News | 3436 | 1705
Norfolk VA | 3411 | 1630
Petersburg VA | 3557 | 1400
Pulaski | 3336 | 1539
Quantico | 4109 | 1232
Richmond | 3883 | 1493
Roanoke | 4246 | 1552
Virginia Beach | 3336 | 1539
Washington DC | 4921 | 1113
Weyers Cave | 4878 | 1102
Winchester | 5193 | 1196
Wise | 4910 | 747
Aberdeen WA | 5240 | 21 | Washington
Bellingham | 5768 | 24
Bremerton | 5533 | 112
Ephrata | 5578 | 882
Everett | 5097 | 69
Forks | 5682 | 19
Hanford | 5669 | 1007
Hoquiam | 5240 | 21
Kelso | 4682 | 115
Moses Lake | 5431 | 641
Olympia | 5331 | 118
Pasco | 4921 | 711
Port Angeles | 5945 | 13
Pullman | 6483 | 234
Renton | 4378 | 216
Seattle | 4372 | 169
Spokane | 6716 | 341
Stampede Pass | 8898 | 81
Tacoma | 5664 | 142
The Dalles | 4501 | 879
Toledo WA | 5853 | 82
Walla Walla | 4836 | 839
Wenatchee | 5748 | 867
Whidbey Island | 5510 | 0
Yakima | 6041 | 430
Beckley | 5361 | 631 | West Virginia
Bluefield | 4451 | 597
Bridgeport | 5137 | 855
Charleston WV | 4708 | 1015
Elkins | 6050 | 368
Huntington | 4642 | 1077
Lewisburg | 6270 | 432
Martinsburg | 4345 | 761
Morgantown | 5020 | 669
Parkersburg | 4979 | 1101
Wheeling | 5793 | 639
Antigo | 8664 | 440 | Wisconsin
Appleton | 7022 | 517
Eau Claire | 8475 | 600
Green Bay | 7853 | 496
Janesville | 6713 | 295
La Crosse | 7445 | 748
Lone Rock | 6651 | 543
Madison | 7724 | 604
Manitowac | 7231 | 322
Marshfield | 7449 | 432
Milwaukee | 7348 | 545
Minocqua | 8772 | 410
Mosinee | 8719 | 401
Oshkosh | 8013 | 380
Phillips | 8638 | 337
Rhinelander | 8823 | 437
Rice Lake | 8706 | 420
Sturgeon Bay | 7301 | 424
Watertown WI | 6864 | 674
Wausau | 7821 | 658
Casper | 7409 | 440 | Wyoming
Cheyenne | 7362 | 265
Cody | 7131 | 436
Evanston | 8339 | 188
Gillette | 6992 | 767
Jackson Hole | 9670 | 15
Lander | 7477 | 432
Laramie | 7799 | 111
Rawlins | 7392 | 289
Riverton | 7579 | 708
Rock Springs | 7971 | 191
Sheridan | 7215 | 399
Worland | 7285 | 611